## 1. Project Summary
JAZEERA ROYAL PALACE 110/13.8 KV S/S - CMC FINAL TECHNICAL REPORT
REPORT METADATA
Document No. | FMSA 24047-FTR-CMC
Enquiry No. | FMSA 24047
Revision | 0
Description | First Issue
Total Pages (main body) | 21
Issue Date | 17 March 2025
Prepared By | NM
Checked By | MM
Approved By | HH
Contractor | FREYSSINET MENARD SAUDI ARABIA
Main Contractor | NESMA INFRASTRUCTURE & TECHNOLOGY
Owner / Client | National Grid / Saudi Electricity Company (SEC)
Project Location | Thuwal, Kingdom of Saudi Arabia
Project Description | Soil Improvement using Controlled Modulus Columns (CMC) for 110/13.8 KV Substation
Reference Geotechnical Report | GBL-GT-24136, Rev.0, June 2024
Site Area | 70m × 60m = 4200 m²
Expected Applied Load | 150 kPa
PROJECT LEVELS
Working Platform Level (EGL) | +6.25 m
Average Existing Ground Level (EGL) — Menard pre-CPTs | +5.90 m
Bottom of Boundary Wall Foundation | +6.55 m
Bottom of Building Foundation and TR Tunnels | +6.85 m
Bottom of Power Transformer Foundation | +7.25 m
Bottom of Auxiliary Tr Foundation | +8.00 m
Bottom of Shunt Reactor Foundation | +8.00 m
Bottom of Outdoor Equipment Foundation | +7.75 m
Average Water Table Level (WTL) | +5.25 m
Groundwater Depth (from N.G.L) | 0.65 to 0.75 m (per geotech report)
SETTLEMENT & BEARING CAPACITY CRITERIA
Required Bearing Capacity | 150 kN/m²
Allowable Settlement - Raft Foundation | 50 mm
Allowable Settlement - Isolated Foundation | 25 mm
Min. CMC Concrete Compressive Strength (28-day) | 25 MPa
Min. LTP Young's Modulus (Ey) | > 65 MPa
REFERENCE DOCUMENTS
Ref. # | Category | Reference Description
[1] | Client's Documents | GEOTECHNICAL INVESTIGATION FOR JAZERA ROYAL PALACE 110/13.8 KV S/S THUWAL – KSA, Report No. GBL-GT-24136, Rev.0, June 2024
[2] | Client's Documents | CMC Design report document reference – FMSA-EN24313-TP
[3] | Client's Documents | Drawings: General Plot Plan, Drawing No. WA 884920 - sheet No. 003 rev. no. 00, dated 2/5/2024
[4] | Standards & Procedures | THE SAUDI BUILDING CODE for SOILS and FOUNDATIONS, SBC 303 – CR, 2018
[5] | Standards & Procedures | ASIRI. 2012. Recommendations for design, construction, and control of rigid inclusion ground improvements, Presses des Ponts
[6] | Standards & Procedures | ASTM. American Society for Testing and Materials
[7] | Standards & Procedures | BS 8006 (1995) Code of Practice for strengthened/reinforced soils and other fills
[8] | Standards & Procedures | MENARD. Quality Assurance and Quality Control System & Procedures
[9] | Standards & Procedures | OHSAS 18001:2007. Occupational Health & Safety Management System
[10] | Standards & Procedures | ISO 14001:2004. Environmental Management System
[11] | Published References | Bowles, J. E. (1997). Foundation Analysis and Design. – 5th Edition. McGraw-Hill
[12] | Published References | Das, B. M. (2007). Principles of Foundation Engineering. – 6th Edition. Thomson Learning
[13] | Published References | Jefferies, M. G., Davies, M. P. (1993). Use of CPTu to Estimate Equivalent SPT N60
[14] | Published References | Kulhawy, F. and Mayne, P. (1990). Manual on Estimating Soil Properties for Foundation Design
[15] | Published References | Lunne T., Robertson P.K., Powell J.J. M. (1997). Cone Penetration Testing in Geotechnical Practice
[16] | Published References | Robertson, P. K., Robertson, K. L. (2015). Guide to Cone Penetration Testing for Geotechnical Engineering. 6th Edition

## 2. Soil Profile Parameters
SOIL PROFILE & DESIGN PARAMETERS (per area)
TABLE 1: SOIL PARAMETERS FOR POWER TRANSFORMER DESIGN
Layer No. | Description | Ey - Young's Modulus (kPa) | γ - Unit Weight (kN/m³) | c' - Cohesion (kPa) | φ' - Internal Friction (°) | υ - Poisson's Ratio
1 | LTP | 60000 | 16 | 0 | 38 | 0.3
2 | Fill material (working platform) | 30000 | 16 | 0 | 28 | 0.3
3 | Fill material | 7500 | 16 | 0 | 29 | 0.3
4 | Sabkha (Drained) | 1260 | 17 | 0 | 27 | 0.3
5 | Clean sand to silty sand | 45000 | 17 | 0 | 27 | 0.3
6 | Clayey silt to silty clay | 15000 | 17 | 20 | 0 | 0.3
7 | Silty sand | 21000 | 17 | 0 | 27 | 0.3
8 | Clayey silt to silty clay | 30000 | 17 | 20 | 0 | 0.3
9 | Silty sand to sandy silt | 36000 | 17 | 0 | 27 | 0.3
10 | Clayey silt to silty clay | 24000 | 17 | 20 | 0 | 0.3
TABLE 2: SOIL PROFILE PARAMETERS FOR BUILDING FOUNDATION AND TR TUNNELS
Layer No. | Description | Ey - Young's Modulus (kPa) | γ - Unit Weight (kN/m³) | c' - Cohesion (kPa) | φ' - Internal Friction (°) | υ - Poisson's Ratio
1 | LTP | 60000 | 16 | 0 | 38 | 0.3
2 | Fill material (working platform) | 30000 | 16 | 0 | 28 | 0.3
3 | Fill material | 3000 | 16 | 0 | 29 | 0.3
4 | Sabkha (Drained) | 1320 | 17 | 0 | 27 | 0.3
5 | Clean sand to silty sand | 24000 | 17 | 0 | 27 | 0.3
6 | Clayey silt to silty clay | 18000 | 17 | 20 | 0 | 0.3
7 | Silty sand to sandy silt | 36000 | 17 | 0 | 27 | 0.3
8 | Clayey silt to silty clay | 24000 | 17 | 20 | 0 | 0.3
TABLE 3: SOIL PARAMETERS FOR BOUNDARY WALL, AUXILIARY TR, SHUNT REACTOR, OUTDOOR EQUIPMENT & REMAINING AREA
Layer No. | Description | Ey - Young's Modulus (kPa) | γ - Unit Weight (kN/m³) | c' - Cohesion (kPa) | φ' - Internal Friction (°) | υ - Poisson's Ratio
1 | LTP | 60000 | 16 | 0 | 38 | 0.3
2 | Fill material (working platform) | 30000 | 16 | 0 | 28 | 0.3
3 | Fill material | 6250 | 17 | 0 | 29 | 0.3
4 | Sabkha (Drained) | 2925 | 17 | 0 | 27 | 0.3
5 | Clean sand to silty sand | 23250 | 17 | 0 | 27 | 0.3
6 | Clayey silt to silty clay | 20000 | 17 | 20 | 0 | 0.3
CPT-TO-YOUNG'S MODULUS CORRELATIONS
Reference |  |  | Lunne & Christofferson (1983), Lunne et al (1997), Bowles (2001)
Sandy soils (Rf ≤ 1.5%) |  |  | Es = (2 to 4) × qc
Silty soils (1.50 < Rf < 3%) — for qc ≤ 2.50 MPa |  |  | Es = 2 × qc
Silty soils (1.50 < Rf < 3%) — for 2.50 < qc ≤ 12.50 MPa |  |  | Es = 4 × qc + 5
Silty soils (1.50 < Rf < 3%) — for qc > 12.50 MPa |  |  | Es = 2 × qc + 20
Clays (Rf ≥ 3%) |  |  | Es = (3 to 8) × qc
CMC Modulus of Elasticity (ASIRI Clause 3.1.1.4) |  |  | Ey = 3700 × fck^(1/3); fck (28-day) ≥ 25 MPa
LEGEND:
• Ey = Young's modulus of layer (kPa)
• γ = Unit weight of layer (kN/m³)
• c' = Effective cohesion (kPa)
• φ' = Effective angle of internal friction (°)
• υ = Poisson's ratio
• LTP = Load Transfer Platform
• Rf = Friction ratio
• qc = CPT tip resistance

## 3. CMC Design Parameters
CMC DESIGN CRITERIA & PARAMETERS
CMC DESIGN METHODOLOGY (per ASIRI 2012 / NF P94-261 / NF P94-262)
Em : Pressure meter modulus |  |  |  | Em = αM × EY (where αM = Rheological factor from Sedran 2003, Briaud 1992, Baguelin 1978, French Standard D60)
qb : Bearing capacity at CMC base (NF P94-262) |  |  |  | qb = Kc × qc (Kc = penetrometer bearing factor; qc = equivalent CPT tip resistance below CMC toe)
Kq : Frank and Zhao factor for end bearing/toe |  |  |  | Fine-grained soils: 11 ¦ Coarse-grained soils: 4.8 (project case)
qnet : Bearing capacity of soil around CMC (NF P94-261) |  |  |  | qnet = Kc × qc = 0.1 × qc (varies based on formation level)
De : Embedment depth |  |  |  | Conservatively assumed = 0
qs : Limit skin friction (NF P94-262) |  |  |  | Function of CPT tip resistance (qc)
KT : Frank and Zhao factor for friction |  |  |  | Fine-grained soils: 2.0 ¦ Coarse-grained soils: 0.8
Ktanδ |  |  |  | Component describing negative skin friction (NF P94-262)
LTP requirement |  |  |  | Well-compacted granular fill; Ey > 65 MPa (compaction by Main Contractor)
TABLE 4: CMC DESIGN PARAMETERS BY AREA
Parameter | Unit | Building Raft and TR Tunnels | Building Isolated Footing | Septic Tank | Power Transformer | Remaining Area | Outdoor Equipment | Boundary Wall | Auxiliary Tr | Shunt Reactor
CMC Diameter | [m] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Total Length | [m] | 18.5 | 17 | 10 | 18.5 | 10 | 12 | 16 | 14 | 14.5
Centre-to-Centre Grid Spacing | [m by m] | 2 × 2 | 2 × 2 | 2 × 2 | 1.80 × 1.80 | 2 × 2 | 2 × 2 | 2 × 2 | 2 × 2 | 2 × 2
Pattern | [-] | Square | Square | Square | Square | Square | Square | Square | Square | Square
NOTES:
• Total length is expressed from the working platform level (varies from +6.5 to +6.7 m).
• CMC Diameter: 600 mm (single value for all areas).
• Minimum Concrete Compressive Strength: 25 MPa.
• Load Transfer Platform (LTP) shall consist of well-compacted granular fill with Ey > 65 MPa. LTP works done by Main Contractor.
• Refusal criteria for installation: 5cm penetration over 2 consecutive minutes.
• Auger diameter: 600 mm, closed at bottom with lost cap.
CMC METHOD OF EXECUTION (Sequence of Works)
Step 1 | Setting out of each future CMC
Step 2a | Driving the special auger into the soil to the desired depth by pushing on the tool and rotating it. Auger diameter is 600 mm, closed at its bottom with a lost cap. Drilling parameters monitored from cabin (drilling speed, depth, torque, etc.).
Step 2b | Before the required depth is reached, the feeding of cement mixture (or concrete) inside the special auger through the stem begins.
Step 2c | When the required depth is reached OR refusal criteria met (5cm penetration over 2 consecutive minutes), driving is stopped.
Step 2d | The auger is then extracted while cement mixture (or concrete) is fed through the stem. Extraction performed without unscrewing. Speed of extraction controlled via Machine Monitor to ensure good filling.
Step 3 | Machine moves to next CMC location.

## 4. Plate Load Tests
APPENDIX 2: PLATE LOAD TEST RESULTS (PLT)
PLT SUMMARY - SETTLEMENT AT DESIGN LOAD (per report Section 6.2)
Test ID | CMC Location |  | Status
PLT-201 | CMC-1043 |  | 0.45 | PASS (< criteria)
PLT-202 | CMC-80 |  | 0.61 | PASS (< criteria)
PLT-203 | CMC-666 |  | 0.36 | PASS (< criteria)
PLT-204 | CMC-942 |  | 0.25 | PASS (< criteria)
Note: Full detailed test data (time-stamped readings at multiple stress levels) included below for the three PLT test certificates available in the report appendix. PLT-203 (CMC-666) detailed certificate is referenced in the summary but not included as appendix data.
PLT-201 / TEST NO. PLT-01 — PILE #1043 (per ASTM D-1194)
Project |  | CMC Piles for Al Jazeera Royal Palance
Client |  | Freyssinet Menard Saudi Arabia Ltd
Location |  | Thuwal - Al Jazeera Royal Palance, Kingdom of Saudi Arabia
Test Location |  | Pile no. 1043
Test Date |  | 17-Dec-2024
REF |  | 2024-6508
Laboratory |  | Applus+ (Building No. 7866, Inkas dist., Rabigh)
Document # |  | SAFCO-QSP-17 / F20 (Issue 01 Jan 2023)
Plate Diameter |  | 45.72 cm
Plate Weight |  | 36.68 kg
Jack Capacity |  | 50.00 ton
Jack Weight |  | 25.0 kg
Stage | Stress (kPa) | Time | Jack Reading (Bar) | Dial Gage 1 (×10⁻²) | Dial Gage 2 (×10⁻²) | Dial Gage 3 (×10⁻²) | Average (×10⁻²) | Settlement (mm) | Temp (°C)
Loading | 0 | 10:25:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 10:28:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 10:31:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 10:34:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 10:37:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 10:40:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 37.5 | 10:43:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 10:46:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 10:49:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 10:52:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 10:55:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 10:58:00 AM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 75 | 11:01:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 11:04:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 11:07:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 11:10:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 11:13:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 11:16:00 AM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 112.5 | 11:19:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 112.5 | 11:22:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 112.5 | 11:25:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 112.5 | 11:28:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 112.5 | 11:31:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 112.5 | 11:34:00 AM | 94 | 11 | 12 | 13 | 12 | 0.12 | 37
Loading | 150 | 11:37:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 150 | 11:40:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 150 | 11:43:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 150 | 11:46:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 150 | 11:49:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 150 | 11:52:00 AM | 125.3 | 18 | 19 | 20 | 19 | 0.19 | 37
Loading | 187.5 | 11:55:00 AM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 187.5 | 11:58:00 AM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 187.5 | 12:01:00 PM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 187.5 | 12:04:00 PM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 187.5 | 12:07:00 PM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 187.5 | 12:10:00 PM | 156.7 | 25 | 26 | 27 | 26 | 0.26 | 38
Loading | 225 | 12:13:00 PM | 188 | 40 | 41 | 42 | 41 | 0.41 | 37
Loading | 225 | 12:28:00 PM | 188 | 41 | 42 | 43 | 42 | 0.42 | 37
Loading | 225 | 12:43:00 PM | 188 | 42 | 43 | 44 | 43 | 0.43 | 37
Loading | 225 | 12:58:00 PM | 188 | 43 | 44 | 45 | 44 | 0.44 | 37
Loading | 225 | 1:13:00 PM | 188 | 44 | 45 | 46 | 45 | 0.45 | 37
Unloading | 150 | 1:16:00 PM | 125.3 | 42 | 43 | 44 | 43 | 0.43 | 37
Unloading | 150 | 1:19:00 PM | 125.3 | 41 | 42 | 43 | 42 | 0.42 | 37
Unloading | 150 | 1:22:00 PM | 125.3 | 40 | 41 | 42 | 41 | 0.41 | 37
Unloading | 150 | 1:25:00 PM | 125.3 | 39 | 40 | 41 | 40 | 0.4 | 37
Unloading | 150 | 1:28:00 PM | 125.3 | 38 | 39 | 40 | 39 | 0.39 | 37
Unloading | 75 | 1:31:00 PM | 62.7 | 30 | 31 | 32 | 31 | 0.31 | 37
Unloading | 75 | 1:34:00 PM | 62.7 | 29 | 30 | 31 | 30 | 0.3 | 37
Unloading | 75 | 1:37:00 PM | 62.7 | 28 | 29 | 30 | 29 | 0.29 | 37
Unloading | 75 | 1:40:00 PM | 62.7 | 27 | 28 | 29 | 28 | 0.28 | 37
Unloading | 75 | 1:43:00 PM | 62.7 | 26 | 27 | 28 | 27 | 0.27 | 37
Unloading | 0 | 1:46:00 PM | 0 | 10 | 11 | 12 | 11 | 0.11 | 37
Unloading | 0 | 1:49:00 PM | 0 | 9 | 10 | 11 | 10 | 0.1 | 37
Unloading | 0 | 1:52:00 PM | 0 | 8 | 9 | 10 | 9 | 0.09 | 37
Unloading | 0 | 1:55:00 PM | 0 | 7 | 8 | 9 | 8 | 0.08 | 37
Unloading | 0 | 1:58:00 PM | 0 | 6 | 7 | 8 | 7 | 0.07 | 37
Settlement Values - PLT-201 (Pile #1043)
Stress Level | Stress (kPa) | Settlement (mm)
Loading - 0 kPa | 0 | 0
Loading - 37.5 kPa | 37.5 | 0.06
Loading - 75 kPa | 75 | 0.09
Loading - 112.5 kPa | 112.5 | 0.12
Loading - 150 kPa (Design) | 150 | 0.19
Loading - 187.5 kPa | 187.5 | 0.26
Loading - 225 kPa (Max) | 225 | 0.45
Unloading - 150 kPa | 150 | 0.39
Unloading - 75 kPa | 75 | 0.27
Unloading - 0 kPa (Residual) | 0 | 0.07
PLT-202 / TEST NO. PLT-02 — PILE #80 (per ASTM D-1194)
Project |  | CMC Piles for Al Jazeera Royal Palance
Client |  | Freyssinet Menard Saudi Arabia Ltd
Location |  | Thuwal - Al Jazeera Royal Palance, Kingdom of Saudi Arabia
Test Location |  | Pile no. 80
Test Date |  | 17-Dec-2024
REF |  | 2024-6508
Laboratory |  | Applus+ (Building No. 7866, Inkas dist., Rabigh)
Document # |  | SAFCO-QSP-17 / F20 (Issue 01 Jan 2023)
Plate Diameter |  | 45.72 cm
Plate Weight |  | 36.68 kg
Jack Capacity |  | 50.00 ton
Jack Weight |  | 25.0 kg
Stage | Stress (kPa) | Time | Jack Reading (Bar) | Dial Gage 1 (×10⁻²) | Dial Gage 2 (×10⁻²) | Dial Gage 3 (×10⁻²) | Average (×10⁻²) | Settlement (mm) | Temp (°C)
Loading | 0 | 2:10:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 2:13:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 2:16:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 2:19:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 2:22:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 0 | 2:25:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 36
Loading | 37.5 | 2:28:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 2:31:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 2:34:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 2:37:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 2:40:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 37.5 | 2:43:00 PM | 31.4 | 5 | 6 | 7 | 6 | 0.06 | 36
Loading | 75 | 2:46:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 2:49:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 2:52:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 2:55:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 2:58:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 75 | 3:01:00 PM | 62.67 | 8 | 9 | 10 | 9 | 0.09 | 37
Loading | 112.5 | 3:04:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 112.5 | 3:07:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 112.5 | 3:10:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 112.5 | 3:13:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 112.5 | 3:16:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 112.5 | 3:19:00 PM | 94 | 14 | 15 | 16 | 15 | 0.15 | 36
Loading | 150 | 3:22:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 150 | 3:25:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 150 | 3:28:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 150 | 3:31:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 150 | 3:34:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 150 | 3:37:00 PM | 125.3 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 187.5 | 3:40:00 PM | 156.7 | 30 | 31 | 32 | 31 | 0.31 | 35
Loading | 187.5 | 3:43:00 PM | 156.7 | 31 | 32 | 33 | 32 | 0.32 | 35
Loading | 187.5 | 3:46:00 PM | 156.7 | 32 | 33 | 34 | 33 | 0.33 | 35
Loading | 187.5 | 3:49:00 PM | 156.7 | 34 | 34 | 35 | 34.3 | 0.34 | 35
Loading | 187.5 | 3:52:00 PM | 156.7 | 35 | 35 | 36 | 35.3 | 0.35 | 35
Loading | 187.5 | 3:55:00 PM | 156.7 | 36 | 36 | 37 | 36.3 | 0.36 | 35
Loading | 225 | 3:58:00 PM | 188 | 56 | 57 | 58 | 57 | 0.57 | 35
Loading | 225 | 4:13:00 PM | 188 | 57 | 58 | 59 | 58 | 0.58 | 35
Loading | 225 | 4:28:00 PM | 188 | 58 | 59 | 60 | 59 | 0.59 | 35
Loading | 225 | 4:43:00 PM | 188 | 59 | 60 | 61 | 60 | 0.6 | 35
Loading | 225 | 4:58:00 PM | 188 | 60 | 61 | 62 | 61 | 0.61 | 35
Unloading | 150 | 5:01:00 PM | 125.3 | 55 | 56 | 57 | 56 | 0.56 | 34
Unloading | 150 | 5:04:00 PM | 125.3 | 55 | 56 | 57 | 56 | 0.56 | 34
Unloading | 150 | 5:07:00 PM | 125.3 | 55 | 56 | 57 | 56 | 0.56 | 34
Unloading | 150 | 5:10:00 PM | 125.3 | 55 | 56 | 57 | 56 | 0.56 | 34
Unloading | 150 | 5:13:00 PM | 125.3 | 55 | 56 | 57 | 56 | 0.56 | 34
Unloading | 75 | 5:16:00 PM | 62.7 | 48 | 49 | 50 | 49 | 0.49 | 37
Unloading | 75 | 5:19:00 PM | 62.7 | 48 | 49 | 49 | 48.7 | 0.49 | 37
Unloading | 75 | 5:22:00 PM | 62.7 | 48 | 49 | 48 | 48.3 | 0.48 | 37
Unloading | 75 | 5:25:00 PM | 62.7 | 48 | 49 | 47 | 48 | 0.48 | 37
Unloading | 75 | 5:28:00 PM | 62.7 | 48 | 49 | 47 | 48 | 0.48 | 37
Unloading | 0 | 5:31:00 PM | 0 | 22 | 21 | 20 | 21 | 0.21 | 37
Unloading | 0 | 5:34:00 PM | 0 | 21 | 20 | 19 | 20 | 0.2 | 37
Unloading | 0 | 5:37:00 PM | 0 | 20 | 19 | 18 | 19 | 0.19 | 37
Unloading | 0 | 5:40:00 PM | 0 | 19 | 18 | 17 | 18 | 0.18 | 37
Unloading | 0 | 5:43:00 PM | 0 | 18 | 17 | 16 | 17 | 0.17 | 37
Settlement Values - PLT-202 (Pile #80)
Stress Level | Stress (kPa) | Settlement (mm)
Loading - 0 kPa | 0 | 0
Loading - 37.5 kPa | 37.5 | 0.06
Loading - 75 kPa | 75 | 0.09
Loading - 112.5 kPa | 112.5 | 0.15
Loading - 150 kPa (Design) | 150 | 0.21
Loading - 187.5 kPa | 187.5 | 0.36
Loading - 225 kPa (Max) | 225 | 0.61
Unloading - 150 kPa | 150 | 0.56
Unloading - 75 kPa | 75 | 0.48
Unloading - 0 kPa (Residual) | 0 | 0.17
PLT-203 / TEST NO. PLT-01 (different cert) — CMC-317 (per ASTM D-1194)
Project |  | Jazeera Palace Substation 110/13.8 KV
Client |  | NESMA INFRASTRUCTURE AND TECHNOLOGY
Location |  | CMC-317
Test Date |  | 2024-11-27
REF |  | RBG-QCR-24-02450
Laboratory |  | Applus+ (different cert)
Document # |  | SAFCO-QSP-17 / F20
Plate Diameter |  | 60.00 cm
Jack Capacity |  | 1000.00 kg/cm²
Stress Units |  | kg/cm² (note: different from PLT-201/202 which use kPa)
Stage | Stress (kg/cm²) | Time | Jack Reading (Bar) | Dial Gage 1 (×10⁻²) | Dial Gage 2 (×10⁻²) | Dial Gage 3 (×10⁻²) | Average (×10⁻²) | Settlement (mm) | Temp (°C)
Loading | 0 | - | 0 | - | - | - | - | - | -
Loading | 0.75 | 11:14:00 AM | 62.8 | 0 | 0 | 0 | 0 | 0 | 34
Loading | 0.75 | 11:17:00 AM | 62.8 | 2 | 2 | 3 | 2.3 | 0.02 | 34
Loading | 0.75 | 11:20:00 AM | 62.8 | 3 | 3 | 4 | 3.3 | 0.03 | 34
Loading | 0.75 | 11:23:00 AM | 62.8 | 4 | 4 | 5 | 4.3 | 0.04 | 34
Loading | 0.75 | 11:26:00 AM | 62.8 | 5 | 5 | 6 | 5.3 | 0.05 | 34
Loading | 0.75 | 11:29:00 AM | 62.8 | 6 | 6 | 7 | 6.3 | 0.06 | 34
Loading | 1.5 | 11:32:00 AM | 125.3 | 10 | 10 | 11 | 10.3 | 0.1 | 34
Loading | 1.5 | 11:35:00 AM | 125.3 | 11 | 11 | 12 | 11.3 | 0.11 | 34
Loading | 1.5 | 11:38:00 AM | 125.3 | 12 | 12 | 13 | 12.3 | 0.12 | 34
Loading | 1.5 | 11:41:00 AM | 125.3 | 13 | 13 | 14 | 13.3 | 0.13 | 34
Loading | 1.5 | 11:44:00 AM | 125.3 | 14 | 14 | 15 | 14.3 | 0.14 | 34
Loading | 1.5 | 11:47:00 AM | 125.3 | 15 | 15 | 16 | 15.3 | 0.15 | 34
Loading | 2.25 | 11:50:00 AM | 188 | 20 | 21 | 22 | 21 | 0.21 | 35
Loading | 2.25 | 11:53:00 AM | 188 | 21 | 22 | 23 | 22 | 0.22 | 35
Loading | 2.25 | 11:56:00 AM | 188 | 22 | 23 | 24 | 23 | 0.23 | 35
Loading | 2.25 | 11:59:00 AM | 188 | 23 | 24 | 25 | 24 | 0.24 | 35
Loading | 2.25 | 12:02:00 PM | 188 | 24 | 25 | 26 | 25 | 0.25 | 35
Loading | 2.25 | 12:05 | 188 | 25 | 26 | 27 | 26 | 0.26 | 35
Loading | 3 | 12:08 | 250.7 | 30 | 31 | 32 | 31 | 0.31 | 35
Loading | 3 | 12:11 | 250.7 | 31 | 32 | 33 | 32 | 0.32 | 35
Loading | 3 | 12:14 | 250.7 | 32 | 33 | 34 | 33 | 0.33 | 35
Loading | 3 | 12:17 | 250.7 | 33 | 34 | 35 | 34 | 0.34 | 35
Loading | 3 | 12:20 | 250.7 | 34 | 35 | 36 | 35 | 0.35 | 35
Loading | 3 | 12:23 | 250.7 | 35 | 36 | 37 | 36 | 0.36 | 35
Unloading | 1.5 | 12:26 | 125.3 | 32 | 33 | 34 | 33 | 0.33 | 35
Unloading | 1.5 | 12:29 | 125.3 | 31 | 32 | 33 | 32 | 0.32 | 35
Unloading | 1.5 | 12:32 | 125.3 | 30 | 31 | 32 | 31 | 0.31 | 35
Unloading | 1.5 | 12:35 | 125.3 | 29 | 30 | 31 | 30 | 0.3 | 35
Unloading | 1.5 | 12:38 | 125.3 | 28 | 29 | 30 | 29 | 0.29 | 35
Unloading | 0 | 12:41 | 0 | 21 | 22 | 24 | 22.3 | 0.22 | 35
Unloading | 0 | 12:44 | 0 | 20 | 21 | 23 | 21.3 | 0.21 | 35
Unloading | 0 | 12:47 | 0 | 19 | 20 | 22 | 20.3 | 0.2 | 35
Unloading | 0 | 12:50 | 0 | 18 | 19 | 21 | 19.3 | 0.19 | 35
Unloading | 0 | 12:53 | 0 | 17 | 18 | 20 | 18.3 | 0.18 | 35
Settlement Values - PLT-203 (CMC-317)
Stress Level | Stress (kg/cm²) | Settlement (mm)
Loading - 0.75 kg/cm² (~75 kPa) | 0.75 | 0.06
Loading - 1.50 kg/cm² (~150 kPa, Design) | 1.5 | 0.15
Loading - 2.25 kg/cm² (~225 kPa, Max) | 2.25 | 0.26
Loading - 3.00kg/cm² (~225 kPa, Max) | 3 | 0.36
Unloading - 1.50 kg/cm² | 1.5 | 0.29
Unloading - 0 (Residual) | 0 | 0.18
PLT-204 / TEST NO. PLT-01 (different cert) — CMC-942 (per ASTM D-1194) | [9 empty] | `
Project |  | Jazeera Palace Substation 110/13.8 KV
Client |  | NESMA INFRASTRUCTURE AND TECHNOLOGY
Location |  | CMC-942
Test Date |  | 15-Dec-2024
REF |  | RBG-QCR-24-02600
Laboratory |  | Applus+ (different cert)
Document # |  | SAFCO-QSP-17 / F20
Plate Diameter |  | 60.00 cm
Jack Capacity |  | 1000.00 kg/cm²
Stress Units |  | kg/cm² (note: different from PLT-201/202 which use kPa)
Stage | Stress (kg/cm²) | Time | Jack Reading (Bar) | Dial Gage 1 (×10⁻²) | Dial Gage 2 (×10⁻²) | Dial Gage 3 (×10⁻²) | Average (×10⁻²) | Settlement (mm) | Temp (°C)
Loading | 0 | - | 0 | - | - | - | - | - | -
Loading | 0.38 | 10:38:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.38 | 10:41:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.38 | 10:44:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.38 | 10:47:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.38 | 10:50:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.38 | 10:53:00 AM | 31.3 | 5 | 5 | 5 | 5 | 0.05 | 34
Loading | 0.75 | 10:56:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 0.75 | 10:59:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 0.75 | 11:02:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 0.75 | 11:05:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 0.75 | 11:08:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 0.75 | 11:11:00 AM | 62.7 | 6 | 7 | 7 | 6.7 | 0.07 | 34
Loading | 1.12 | 11:14:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.12 | 11:17:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.12 | 11:20:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.12 | 11:23:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.12 | 11:26:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.12 | 11:29:00 AM | 94 | 9 | 10 | 11 | 10 | 0.1 | 35
Loading | 1.5 | 11:32:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.5 | 11:35:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.5 | 11:38:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.5 | 11:41:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.5 | 11:44:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.5 | 11:47:00 AM | 125.3 | 13 | 14 | 15 | 14 | 0.14 | 35
Loading | 1.87 | 11:50:00 AM | 156.7 | 15 | 16 | 17 | 16 | 0.16 | 35
Loading | 1.87 | 11:53:00 AM | 156.7 | 15 | 16 | 17 | 16 | 0.16 | 35
Loading | 1.87 | 11:56:00 AM | 156.7 | 15 | 16 | 17 | 16 | 0.16 | 35
Loading | 1.87 | 11:59:00 AM | 156.7 | 15 | 16 | 17 | 16 | 0.16 | 35
Loading | 1.87 | 12:02:00 PM | 156.7 | 15 | 16 | 17 | 16 | 0.16 | 35
Loading | 2.25 | 12:20:00 PM | 188 | 19 | 20 | 21 | 20 | 0.2 | 35
Loading | 2.25 | 12:35:00 PM | 188 | 19 | 20 | 21 | 20 | 0.2 | 35
Loading | 2.25 | 12:50:00 PM | 188 | 21 | 22 | 23 | 22 | 0.22 | 35
Loading | 2.25 | 1:05:00 PM | 188 | 24 | 25 | 26 | 25 | 0.25 | 35
Loading | 2.25 | 1:20:00 PM | 188 | 24 | 25 | 26 | 25 | 0.25 | 35
Loading | 2.25 | 1:35:00 PM | 188 | 24 | 25 | 26 | 25 | 0.25 | 35
Unloading | 1.5 | 1:38:00 PM | 125.3 | 23 | 24 | 25 | 24 | 0.24 | 35
Unloading | 1.5 | 1:41:00 PM | 125.3 | 23 | 24 | 25 | 24 | 0.24 | 35
Unloading | 1.5 | 1:44:00 PM | 125.3 | 23 | 24 | 25 | 24 | 0.24 | 35
Unloading | 1.5 | 1:47:00 PM | 125.3 | 23 | 24 | 25 | 24 | 0.24 | 35
Unloading | 1.5 | 1:50:00 PM | 125.3 | 23 | 24 | 25 | 24 | 0.24 | 35
Unloading | 0.75 | 1:53:00 PM | 62.7 | 20 | 21 | 21 | 20.7 | 0.21 | 35
Unloading | 0.75 | 1:56:00 PM | 62.7 | 19 | 20 | 20 | 19.7 | 0.2 | 35
Unloading | 0.75 | 1:59:00 PM | 62.7 | 19 | 20 | 20 | 19.7 | 0.2 | 35
Unloading | 0.75 | 2:02:00 PM | 62.7 | 19 | 20 | 20 | 19.7 | 0.2 | 35
Unloading | 0.75 | 2:05:00 PM | 62.7 | 19 | 20 | 20 | 19.7 | 0.2 | 35
Unloading | 0.75 | 2:08:00 PM | 62.7 | 19 | 20 | 20 | 19.7 | 0.2 | 35
Unloading | 0 | 2:11:00 PM | 0 | 11 | 12 | 13 | 12 | 0.12 | 35
Unloading | 0 | 2:14:00 PM | 0 | 10 | 11 | 12 | 11 | 0.11 | 35
Unloading | 0 | 2:17:00 PM | 0 | 10 | 11 | 12 | 11 | 0.11 | 35
Unloading | 0 | 2:20:00 PM | 0 | 10 | 11 | 12 | 11 | 0.11 | 35
Settlement Values - PLT-204 (CMC-942)
Stress Level | Stress (kg/cm²) | Settlement (mm)
Loading - 0.38 kg/cm² (~37.5 kPa) | 0.38 | 0.05
Loading - 0.75 kg/cm² (~75 kPa) | 0.75 | 0.07
Loading - 1.12 kg/cm² (~112.5 kPa) | 1.12 | 0.1
Loading - 1.50 kg/cm² (~150 kPa, Design) | 1.5 | 0.14
Loading - 1.87 kg/cm² (~187.5 kPa) | 1.87 | 0.16
Loading - 2.25 kg/cm² (~225 kPa, Max) | 2.25 | 0.25
Unloading - 1.50 kg/cm² | 1.5 | 0.24
Unloading - 0.75 kg/cm² | 0.75 | 0.2
Unloading - 0 (Residual) | 0 | 0.11

## 5. Zone Load Test
APPENDIX 3: ZONE LOAD TEST (ZLT-201) RESULTS
ZLT-201 TEST PARAMETERS
Test ID |  | ZLT-201 (Sub Station Building)
Report No. |  | Job No: GC/10373JO/17823/24
Laboratory |  | Gulf Consult (Geotechnical Division), Alkhobar, Saudi Arabia
Client |  | Saudi Water Authority (SWA)
Project |  | Al Jazeera Palace Sub Station Project
Date of Test |  | 22-Dec-2024
Report Date |  | 24/12/2024
Test Foundation Size |  | 2.0 m × 2.0 m (Steel Test Plate)
Soil Description / CMC Tested |  | CMC #155, #156, #172, #173 (4 CMCs)
Design Bearing Pressure |  | 150 kN/m²
Maximum Test Pressure (150% of design) |  | 225 kN/m²
CMC Diameter |  | 600 mm
Number of Dial Gauges |  | 4 (calibrated, 0.01 mm accuracy, 100 mm capacity)
Reference Beams |  | 2 (with 4 dial gauges mounted)
ZLT-201: SUMMARY OF LOAD VERSUS SETTLEMENT READINGS (TABLE-1)
% of Proposed Load | Applied Pressure (kN/m²) | Applied Load (kN) | Average Total Settlement (mm) | Actual Holding Time | Stage / Remarks
0 | 0 | 0 | 0 | 15 Minutes | Loading Stage
25 | 38 | 150 | 0.642 | 15 Minutes | Loading Stage
0 | 0 | 0 | 0.117 | 15 Minutes | Loading Stage
25 | 38 | 150 | 0.717 | 1 Hour | Loading Stage
50 | 75 | 300 | 1.295 | 1 Hour | Loading Stage
75 | 113 | 450 | 2.2 | 1 Hour | Loading Stage
100 | 150 | 600 | 3.36 | 1 Hour | Loading Stage (Design Load)
125 | 188 | 750 | 4.732 | 1 Hour | Loading Stage
150 | 225 | 900 | 6.29 | 2 Hours | Loading Stage (Maximum Test Pressure)
125 | 188 | 750 | 6.272 | 30 Minutes | Unloading Stage
100 | 150 | 600 | 6.177 | 30 Minutes | Unloading Stage
75 | 113 | 450 | 5.99 | 30 Minutes | Unloading Stage
50 | 75 | 300 | 5.797 | 30 Minutes | Unloading Stage
25 | 38 | 150 | 5.415 | 30 Minutes | Unloading Stage
0 | 0 | 0 | 4.51 | 30 Minutes | Unloading Stage (Residual)
ZLT-201: SUMMARY OF TEST RESULTS (TABLE-3)
Test Number | Settlement under 150 kN/m² (Design Bearing) - mm | Settlement under 225 kN/m² (Max Applied = 150% Safe Bearing) - mm | Residual Settlement (mm)
ZLT1 - Station Building | 3.36 | 6.29 | 4.51
ZLT-201 CONCLUSION
• No shear failure was observed up to the maximum test pressure of 225 kN/m².
• Footing settlement at design pressure of 150 kN/m² is 3.360 mm (PASS - well below 50 mm allowable).
• Footing settlement at maximum test pressure of 225 kN/m² is 6.290 mm.
• Residual settlement is 4.510 mm.
ZLT-201 TEST PROCEDURE NOTES
• Precast concrete footing placed on test location.
• After centering test plate, 4 calibrated dial gauges mounted on reference beams at 90° intervals, equidistant from sides of footing.
• Load applied in 25% increments of safe bearing pressure of 38 kN/m² up to maximum test pressure of 225 kN/m².
• Loading: 3 increments with 15-min holding time, 5 increments with 1-hour holding time, 2-hour at max.
• Unloading: 4 decrements with 30-min holding time each; at zero load, 30 min holding to record rebound.
• Settlement recorded immediately after each load increment/decrement, with additional readings at 0, 1.5, 3, 5, 15, 25, 30, 45 & 60 minutes.
• For longer holding durations, additional readings taken at 30-minute intervals.

## 6. Pile Integrity Tests
APPENDIX 4: PILE INTEGRITY TEST (PIT) RESULTS - 55 PILES
PIT REPORT INFORMATION
Test Date |  |  | 21-Dec-2024
Report Date |  |  | 3-Feb-2025
Total Piles Tested (PIT Report) |  |  | 55 (50 detailed reflectograms included)
Test Method |  |  | Pile Integrity Test (PIT) - Low Strain Method
Equipment |  |  | PIT Collector device + 1 lb. hand-held hammer with integral cushion and accelerometer
Wave Velocity Assumption |  |  | 4000 m/s (sound concrete)
Pile Diameter |  |  | 60 cm (CMC)
Pile Length Range |  |  | 10.0 m to 18.5 m
Engineer / Checked By |  |  | ALI ALKAAF
Approved By |  |  | ALI ALKAAF
Hammer Blows per Test |  |  | 3 blows averaged
Number of Reflectograms |  |  | 55 individual pile records
DETAILED PIT RECORDS - ALL 50 PILES
Sr. No. | Test Date | Pile No. | Wave Velocity C (m/s) | Amplitude (Amp) | Frequency F | Planned Length (m) | Average (Avg)
1 | 12/21/2024 | 584 | 4000 | 85 | 0 | 15 | 15
2 | 12/21/2024 | 520 | 4000 | 85 | 0 | 15 | 15
3 | 12/21/2024 | 295 | 4000 | 101.1 | 0 | 17.3 | 15
4 | 12/21/2024 | 579 | 4000 | 101.1 | 0 | 10 | 15
5 | 12/21/2024 | 551 | 4000 | 85 | 0 | 15 | 19
6 | 12/21/2024 | 596 | 4000 | 85 | 0 | 10 | 15
7 | 12/21/2024 | 572 | 4000 | 10 | 0 | 10 | 15
8 | 12/21/2024 | 569 | 4000 | 85 | 0 | 10 | 16
9 | 12/21/2024 | 542 | 4000 | 85 | 0 | 15 | 15
10 | 12/21/2024 | 866 | 4000 | 85 | 0 | 10 | 15
11 | 12/21/2024 | 328 | 4000 | 95 | 0 | 17 | 15
12 | 12/21/2024 | 319 | 4000 | 95 | 0 | 17 | 15
13 | 12/21/2024 | 590 | 4000 | 85 | 0 | 14.5 | 15
14 | 12/21/2024 | 317 | 4000 | 95 | 0 | 17 | 16
15 | 12/21/2024 | 891 | 4000 | 60 | 0 | 10 | 15
16 | 12/21/2024 | 280 | 4000 | 100 | 0 | 18.5 | 15
17 | 12/21/2024 | 232 | 4000 | 95 | 0 | 16.5 | 15
18 | 12/21/2024 | 265 | 4000 | 100 | 0 | 18.2 | 15
19 | 12/21/2024 | 263 | 4000 | 100 | 0 | 18.2 | 15
20 | 12/21/2024 | 248 | 4000 | 100 | 0 | 10 | 15
21 | 12/21/2024 | 996 | 4000 | 100 | 0 | 18.2 | 15
22 | 12/21/2024 | 1026 | 4000 | 100 | 0 | 18.3 | 15
23 | 12/21/2024 | 1027 | 4000 | 100 | 0 | 18 | 15
24 | 12/21/2024 | 1043 | 4000 | 100 | 0 | 18.1 | 15
25 | 12/21/2024 | 1071 | 4000 | 100 | 0 | 18.4 | 15
26 | 12/21/2024 | 1088 | 4000 | 100 | 0 | 18 | 15
27 | 12/21/2024 | 87 | 4000 | 100 | 0 | 18 | 15
28 | 12/21/2024 | 41 | 4000 | 102.6 | 0 | 18.5 | 15
29 | 12/21/2024 | 44 | 4000 | 85 | 0 | 15.5 | 15
30 | 12/21/2024 | 48 | 4000 | 100 | 0 | 18 | 15
31 | 12/21/2024 | 969 | 4000 | 85 | 0 | 14.5 | 15
32 | 12/21/2024 | 116 | 4000 | 95 | 0 | 17 | 17
33 | 12/21/2024 | 112 | 4000 | 100 | 0 | 18.5 | 15
34 | 12/21/2024 | 160 | 4000 | 100 | 0 | 18.3 | 15
35 | 12/21/2024 | 196 | 4000 | 100 | 0 | 10 | 15
36 | 12/21/2024 | 320 | 4000 | 95 | 0 | 17 | 15
37 | 12/21/2024 | 313 | 4000 | 90 | 0 | 16 | 15
38 | 12/21/2024 | 930 | 4000 | 85 | 0 | 14.5 | 15
39 | 12/21/2024 | 391 | 4000 | 85 | 0 | 10 | 15
40 | 12/21/2024 | 652 | 4000 | 85 | 0 | 10 | 15
41 | 12/21/2024 | 669 | 4000 | 85 | 0 | 10 | 15
42 | 12/21/2024 | 779 | 4000 | 85 | 0 | 10 | 17
43 | 12/21/2024 | 1098 | 4000 | 85 | 0 | 10 | 15
44 | 12/21/2024 | 402 | 4000 | 85 | 0 | 10 | 16
45 | 12/21/2024 | 406 | 4000 | 85 | 0 | 10 | 15
46 | 12/21/2024 | 757 | 4000 | 85 | 0 | 10 | 15
47 | 12/21/2024 | 471 | 4000 | 85 | 0 | 15 | 15
48 | 12/21/2024 | 67 | 4000 | 100 | 0 | 18 | 15
49 | 12/21/2024 | 1013 | 4000 | 10 | 0 | 10 | 15
50 | 12/21/2026 | 396 | 4000 | 10 | 0 | 10 | 15
51 | 2024-11-28 | 819 | 4000 | 10 | 0 | 10 | 15
52 | 2024-11-28 | 815 | 4000 | 10 | 0 | 10 | 16
53 | 2024-11-28 | 691 | 4000 | 10 | 0 | 10 | 15
54 | 2024-11-28 | 680 | 4000 | 10 | 0 | 10 | 15
55 | 2024-11-28 | 399 | 4000 | 10 | 0 | 10 | 15
PIT CONCLUSION
• Fifty-five (55) cast-in-situ CMC piles tested using Pile Integrity Tester device.
• Test results show wave velocity from pile top to its toe against depth below pile top.
• Sound concrete wave velocity assumed: 4000 m/s.
• Any deviation of the plot from a sound pile (straight line) indicates presence of changes in cross-sectional area or cracks.
• Test purpose: indicate pile integrity, identify cracks or major reduction in cross-sectional area.
• Note: At time of testing, several CMC heads were not exposed (under backfilling) or not leveled — see field notes in PIT report.
• Note: Some piles had not reached 7th day age at time of test.

## 7. Concrete Compressive
APPENDIX 5: CONCRETE COMPRESSIVE TEST RESULTS - CYLINDER TESTS FOR CMC
CYLINDER TEST RESULTS FOR CMC - SUMMARY INFO
Project |  |  | Construction of Jazera Royal Palace 110/13.8 kV Substation Thuwal
Test Type |  |  | Cylinder Compressive Test
Specimen Type |  |  | Concrete Cylinder
Number of Batches |  |  | 41 batches
Total Number of CMCs Tested |  |  | 1,021 CMCs (sum of all batches)
Test Ages |  |  | 7 Days and 28 Days
Minimum Required Compressive Strength (per design) |  |  | 25 MPa (N/mm²)
Test Period (Casting Dates) |  |  | 14-Oct-2024 to 16-Dec-2024
Test Period (28-day Testing) |  |  | 11-Nov-2024 to 13-Jan-2025
DETAILED CONCRETE COMPRESSIVE TEST RESULTS - ALL 41 BATCHES
S. No. | CMC ID Numbers | No. of CMC Cast | Date of Casting | 7-Day Test Date | 28-Day Test Date | 7-Day Strength (N/mm²) | 28-Day Strength (N/mm²) | Result
1 | 386, 415, 417, 419, 421, 423, 827, 828 and 859 | 9 | 14-Oct-24 | 21-Oct-24 | 11-Nov-24 | 37.5 | 47.2 | PASS
2 | 387, 388, 389, 390, 665, 666, 676, 686, 696, 812, 813, 814, 815, 820, 821, 822, 823, 829, 830, 842, 855, 856 and 857 | 23 | 15-Oct-24 | 22-Oct-24 | 12-Nov-24 | 36.1 | 44.7 | PASS
3 | 684 | 1 | 16-Oct-24 | 23-Oct-24 | 13-Nov-24 | 40.7 | 48 | PASS
4 | 391, 392, 393, 394, 395, 396, 397, 658, 659, 660, 661, 662, 663, 664, 669, 670, 671, 672, 673, 674, 675, 679, 680, 681, 682, 683, 685, 690, 691, 692, 693, 694, 695, 836, 837, 838, 839, 840 and 841 | 39 | 17-Oct-24 | 24-Oct-24 | 14-Nov-24 | 33.1 | 46.4 | PASS
5 | 398, 399, 657, 667, 668, 677, 678, 687, 799, 688, 689, 833, 834 and 835 | 14 | 21-Oct-24 | 28-Oct-24 | 18-Nov-24 | 38.9 | 47.8 | PASS
6 | 400, 401, 402, 403, 404, 405, 763, 765, 769, 770, 775, 776, 777, 778, 781, 782, 783, 784, 787, 788, 789, 790, 793, 794, 795, 796, 800, 801, 802, 850, 851, 852, 853 and 854 | 34 | 22-Oct-24 | 29-Oct-24 | 19-Nov-24 | 38.6 | 47.9 | PASS
7 | 409, 410, 411, 466, 468, 470, 472, 474, 735, 736, 739, 740, 744, 745, 746, 749, 750, 754, 843, 844 and 858 | 21 | 23-Oct-24 | 30-Oct-24 | 20-Nov-24 | 39.2 | 45.3 | PASS
8 | 406, 407, 408, 737, 738, 741, 742, 743, 747, 748, 751, 752, 753, 757, 758, 759, 760, 764, 845, 846, 847 and 848 | 22 | 24-Oct-24 | 31-Oct-24 | 21-Nov-24 | 28.9 | 48.6 | PASS
9 | 607, 608, 609, 610, 611, 612, 613, 614, 617, 618, 619, 620, 621, 622, 623, 627, 628, 629, 630, 631, 632, 633, 637, 638, 639, 640, 641, 642, 643, 647, 648, 649, 650, 651, 652, 653, 766, 771, 772, 776, 779, 780, 785, 786, 791, 792, 797, 798, 804, 805, 806, 807 and 849 | 52 | 26-Oct-24 | 2-Nov-24 | 23-Nov-24 | 37.6 | 47.2 | PASS
10 | 422, 425, 424, 426, 428, 430, 431, and 982 | 8 | 28-Oct-24 | 4-Nov-24 | 25-Nov-24 | 38.4 | 46.4 | PASS
11 | 427, 429, 615, 616, 624, 625, 626, 634, 635, 636, 644, 645, 646, 654, 655, 656, 808, 809, 810, 811, 816, 817, 818, 819, 824, 825, 826, 899, 900, 901, 983 and 984 | 32 | 29-Oct-24 | 5-Nov-24 | 26-Nov-24 | 36.5 | 47 | PASS
12 | 475, 477, 479, 481, 483, 484 and 485 | 7 | 30-Oct-24 | 6-Nov-24 | 27-Nov-24 | 27.8 | 45.9 | PASS
13 | 308, 309, 310, 311, 476, 478, 480, 482, 697, 718, 720, 721, 722, 724, 725, 726, 727, 729, 730, 731, 732 and 734 | 22 | 31-Oct-24 | 7-Nov-24 | 28-Nov-24 | 27.7 | 42.2 | PASS
14 | 1, 2, 372, 373, 374, 375, 376, 377, 378, 379, 380, 381, 382, 383, 384, 385, 464, 465, 467, 469, 471, 473, 723, 728, 733, 755, 756, 761, 762, 767, 768, 773, 774, 803, 1097, 1098 and 1099 | 37 | 2-Nov-24 | 9-Nov-24 | 30-Nov-24 | 26.7 | 47.2 | PASS
15 | 360, 361, 362, 363, 364, 365, 366, 367, 368, 369, 370, 371, 412, 413, 414, 416, 418, 420, 437, 439, 440, 937, 938, 939, 941, 942, 943, 947, 949, 950, 951, 957 and 959 | 33 | 3-Nov-24 | 10-Nov-24 | 1-Dec-24 | 27.7 | 46.3 | PASS
16 | 435, 441, 486, 487, 488, 489, 490, 491, 492, 493, 698, 699, 700, 701, 933, 934, 935, 958, 971, 1070, 1075, 1076, 1077 | 33 | 4-Nov-24 | 11-Nov-24 | 2-Dec-24 | 27.2 | 45.8 | PASS
17 | 3, 5, 7, 9, 10, 11, 13, 17, 19, 21, 33, 35, 37, 39, 358, 359, 452, 454, 456, 457, 458, 459, 460, 461, 462, 463, 534, 535, 560, 561, 589, 591, 592, 860, 902, 903, 908, 909, 1083, 1087 and 1089 | 41 | 5-Nov-24 | 12-Nov-24 | 3-Dec-24 | 29.1 | 47.1 | PASS
18 | 18, 23, 25, 27, 29, 31, 41, 43, 45, 47, 49, 55, 57, 59, 61, 63, 65, 69, 71, 73, 75, 77, 79, 81, 83, 432, 434, 960, 963, 964, 967, 968, 972, 979, 980 and 981 | 36 | 6-Nov-24 | 13-Nov-24 | 4-Dec-24 | 41.5 | 45.8 | PASS
19 | 92, 94, 96, 98, 100, 110, 112, 114, 116, 127, 128, 130, 132, 134, 144, 146, 148, 150, 944, 948, 952, 974, 975, 976 and 977 | 25 | 7-Nov-24 | 14-Nov-24 | 5-Dec-24 | 37.7 | 40.7 | PASS
20 | 91, 93, 107, 109, 125, 141, 143, 318, 327, 330, 536, 537, 538, 539, 540, 541, 543, 546, 562, 563, 564, 565, 566, 567, 569, 571, 599, 831, 861, 863, 865, 877, 878, 879, 880 and 916 | 36 | 9-Nov-24 | 16-Nov-24 | 7-Dec-24 | 39.4 | 45 | PASS
21 | 24, 26, 28, 30, 32, 40, 42, 44, 46, 48, 433, 961, 962, 965, 966, 969 and 970 | 17 | 19-Nov-24 | 26-Nov-24 | 17-Dec-24 | 30.7 | 47 | PASS
22 | 20, 131, 133, 149, 151, 165, 166, 167, 168, 181, 182, 183, 184, 185, 442, 929, 930, 931, 932, 936, 940, 973 and 1095 | 23 | 21-Nov-24 | 28-Nov-24 | 19-Dec-24 | 42.3 | 52.5 | PASS
23 | 4, 6, 8, 12, 14, 15, 16, 22, 34, 36, 38, 66, 82, 117, 436, 438, 945, 946, 953, 954, 955, 956, 978, 1082, 1088 and 1093 | 26 | 23-Nov-24 | 30-Nov-24 | 21-Dec-24 | 37.15 | 45.5 | PASS
24 | 54, 56, 58, 60, 62, 64, 72, 74, 76, 78, 80, 88, 89, 90, 95, 97, 99, 105, 106, 108, 111, 113 and 115 | 23 | 24-Nov-24 | 1-Dec-24 | 22-Dec-24 | 36.1 | 45.7 | PASS
25 | 50, 51, 52, 53, 67, 68, 70, 84, 85, 86, 87, 101, 102, 103, 104, 1060, 1061, 1062, 1063, 1064, 1065, 1066, 1067, 1068, 1069, 1071, 1072, 1073, 1074 and 1078 | 30 | 25-Nov-24 | 2-Dec-24 | 23-Dec-24 | 35.4 | 45.8 | PASS
26 | 123, 124, 126, 129, 140, 142, 145, 147, 157, 158, 159, 160, 161, 162, 163, 164, 173, 174, 175, 176, 177, 178, 179, 180, 494, 495, 496, 497, 702 and 703 | 30 | 26-Nov-24 | 3-Dec-24 | 24-Dec-24 | 35.7 | 46.2 | PASS
27 | 118, 119, 120, 121, 122, 135, 136, 137, 138, 139, 152, 153, 154, 155, 156, 169, 170, 171, 172, 542, 544, 545, 547, 568, 570, 572, 573, 600, 601, 832, 862, 864, 866, 867, 868, 869, 870, 871, 1041, 1042, 1043, 1044, 1047, 1048, 1049, 1052, 1053, 1054, 1057, 1058 and 1059 | 51 | 27-Nov-24 | 4-Dec-24 | 25-Dec-24 | 34.2 | 54.5 | PASS
28 | 344, 443, 444, 445, 498, 499, 500, 501, 502, 503, 504, 505, 704, 705, 706, 707, 917, 918, 919, 920, 921, 922, 923, 924, 925, 926, 927, 928, 1035, 1036, 1037, 1038, 1039, 1040, 1045, 1046, 1050, 1051, 1055 and 1056 | 40 | 28-Nov-24 | 5-Dec-24 | 26-Dec-24 | 34.9 | 51.1 | PASS
29 | 186, 188, 190, 192, 194, 196, 198, 201, 203, 205, 207, 209, 212, 214, 216, 218, 220, 222, 223, 225, 227, 229, 231, 233, 312, 321, 343, 346, 347, 357, 896, 1019, 1023, 1029, 1033 and 1096 | 36 | 30-Nov-24 | 7-Dec-24 | 28-Dec-24 | 36.3 | 50.2 | PASS
30 | 446, 449, 450, 453, 507, 508, 511, 512, 586, 588, 708, 710, 905, 907, 910, 912, 1015, 1017, 1021, 1025, 1027 and 1031 | 22 | 1-Dec-24 | 8-Dec-24 | 29-Dec-24 | 38.5 | 49.9 | PASS
31 | 236, 242, 244, 246, 247, 255, 257, 266, 268, 270, 271, 279, 281, 316, 323, 324, 325, 331, 337, 340, 341, 892 and 894 | 23 | 2-Dec-24 | 9-Dec-24 | 30-Dec-24 | 33.4 | 46.6 | PASS
32 | 238, 240, 249, 251, 253, 260, 262, 264, 273, 275, 277, 319, 332, 455, 590, 913, 915, 994, 995, 997, 1001, 1003, 1004, 1007, 1011 and 1013 | 26 | 3-Dec-24 | 10-Dec-24 | 31-Dec-24 | 36.5 | 43.4 | PASS
33 | 285, 287, 289, 290, 291, 292, 301, 303, 305, 306, 307, 326, 328, 329, 333, 335, 336, 355, 356, 593, 594, 596, 598, 873, 875, 881, 883, 895, 898 and 914 | 30 | 4-Dec-24 | 11-Dec-24 | 1-Jan-25 | 36.2 | 45 | PASS
34 | 526, 527, 528, 529, 531, 532, 533, 548, 550, 552, 554, 556, 558, 575, 577, 579, 581, 583, 585, 595, 597, 602, 604, 719, 874, 882, 885, 887 and 889 | 29 | 5-Dec-24 | 12-Dec-24 | 2-Jan-25 | 36.8 | 45.5 | PASS
35 | 189, 191, 193, 195, 197, 199, 204, 206, 208, 210, 211, 217, 219, 221, 228, 230, 232, 234, 235, 313, 315, 320, 322, 345, 348, 349, 350, 447, 897 and 904 | 30 | 8-Dec-24 | 15-Dec-24 | 5-Jan-25 | 36.7 | 46.8 | PASS
36 | 187, 200, 202, 213, 215, 224, 226, 506, 509, 510, 513, 514, 517, 518, 521, 709, 711, 713, 715, 1010, 1012, 1014, 1016, 1018, 1020, 1022, 1024, 1026, 1028, 1030, 1032 and 1034 | 32 | 9-Dec-24 | 16-Dec-24 | 6-Jan-25 | 35.8 | 43.9 | PASS
37 | 245, 258, 259, 269, 282, 314, 317, 334, 338, 339, 342, 351, 352, 353, 354, 448, 451, 587, 891, 893, 906 and 911 | 22 | 10-Dec-24 | 17-Dec-24 | 7-Jan-25 | 37.1 | 43.7 | PASS
38 | 237, 239, 241, 243, 248, 250, 252, 254, 256, 261, 263, 265, 267, 272, 274, 276, 278, 280, 515, 516, 519, 990, 992, 996, 1005 and 1008 | 26 | 11-Dec-24 | 18-Dec-24 | 8-Jan-25 | 35.8 | 45.1 | PASS
39 | 294, 297, 520, 522, 525, 603, 605, 606, 712, 714, 717, 872, 985, 987, 988, 991, 993, 998, 999, 1000, 1002, 1006 and 1009 | 23 | 12-Dec-24 | 19-Dec-24 | 9-Jan-25 | 36.8 | 45.2 | PASS
40 | 284, 288, 296, 298, 300, 530, 551, 553, 555, 557, 559, 576, 578, 580, 582, 584, 876, 884, 886, 888, 890 and 989 | 22 | 14-Dec-24 | 21-Dec-24 | 11-Jan-25 | 34.2 | 46.7 | PASS
41 | 283, 286, 293, 295, 299, 302, 304, 523, 524, 549, 574, 716 and 986 | 13 | 16-Dec-24 | 23-Dec-24 | 13-Jan-25 | 33.7 | 46.8 | PASS
STATISTICS SUMMARY
Metric | Value
Total CMCs Cast (sum of all batches) | 1099
Total Number of Batches | 41
Average 7-Day Strength (N/mm²) | 35.2329
Minimum 7-Day Strength (N/mm²) | 26.7
Maximum 7-Day Strength (N/mm²) | 42.3
Average 28-Day Strength (N/mm²) | 46.5756
Minimum 28-Day Strength (N/mm²) | 40.7
Maximum 28-Day Strength (N/mm²) | 54.5
Required Min Strength (Design) | 25
Number of Batches PASSING | 41
Number of Batches FAILING | 0