## 1. Project & BH Summary
GEOTECHNICAL INVESTIGATION FOR JAZERA ROYAL PALACE 110/13.8 KV S/S - THUWAL, KSA
PROJECT INFORMATION
Report No. | GBL-GT-24136
Revision No. | Rev.0
Status | Final Report
Date | June 2024
Prepared For | NESMA INFRASTRUCTURE & TECHNOLOGY, JEDDAH - KSA
Project Location | Thuwal, KSA
Project Description | Construction of facilities and buildings for 110/13.8 KV Substation
Prepared By | Engr. M. Ali (Geotechnical Engineer)
Reviewed By | Engr. M. Daniyal (Geotechnical Manager)
Approved By | Engr. Mahmoud Alhamawi (Technical Manager)
Purchase Order Ref. | 8699-0, dated 18th April, 2024
SITE DESCRIPTION
The site is a vacant plot that is generally flat. Bounded by vacant plots on all sides except south side. At the time of investigation, the site was unoccupied. No high voltage, electrical or telephone poles, sewer or water pipes were observed within the depth of the drilled boreholes.
TABLE 1: SEISMICITY AND EARTHQUAKES (per SBC 301-CR-18 / SBC 301-2008)
Parameter | Value | Reference Standard
Mapped Spectral Response Acceleration for short Period (0.2 Sec.), Ss | 20 | SBC 301-CR-18 Figure 22-1
Mapped Spectral Response Acceleration for 1-Second, S1 | 4 | SBC 301-CR-18 Figure 22-2
Standard Penetration Resistance, N | <15 | SBC 301-CR-18 Table 20-1
Soil Profile | E | SBC 301-CR-18 Table 20-1
Fa (Site coefficient) | 0.9 | SBC 301-CR-18 Table 11-1
Fv (Site coefficient) | 2.4 | SBC 301-CR-18 Table 11-2
TABLE 2: BOREHOLES DETAILS
BH No. | Northing | Easting | Ground Water Level (m) | Date of Drilling (Start/Finish) | Depth (m)
BH-1 | 2443920.0645 | 502967.6916 | 0.65 | 06-Jun-24 / 06-Jun-24 | 15
BH-2 | 2443934.5346 | 502992.9425 | 0.7 | 07-Jun-24 / 07-Jun-24 | 15
BH-3 | 2443943.6023 | 503008.4722 | 0.7 | 07-Jun-24 / 07-Jun-24 | 10
BH-4 | 2443951.8936 | 502964.9887 | 0.75 | 07-Jun-24 / 07-Jun-24 | 10
BH-5 | 2443911.7517 | 502986.385 | 0.7 | 07-Jun-24 / 07-Jun-24 | 12
BH-1 (OUT) | 2443875 | 502898 | 1.15 | 04-Jun-24 / 04-Jun-24 | 15
BH-2 (OUT) | 2443860 | 502872 | 1.1 | 04-Jun-24 / 04-Jun-24 | 15
SUBSURFACE STRATIGRAPHY
Layer | Description
Fill Material | Brownish, loose to medium dense, backfill material - found in all boreholes |  |  |  | 0.0 m to 0.75 m
Sabkha | Dark gray, very loose Sabkha - found in all boreholes |  |  |  | 0.75 m to 4.5 m
Silty Sand | Dark gray, very loose to medium dense Silty Sand - found in all boreholes |  |  |  | 4.5 m to 12.0 m
Lean Clay with Sand | Brownish, stiff to very stiff Lean Clay with Sand - found in some boreholes |  |  |  | 12.0 m to 15.0 m

## 2. Design Parameters & Recs
DESIGN PARAMETERS & FOUNDATION RECOMMENDATIONS
TABLE 10: SOIL PARAMETERS AS PER SITE CONDITIONS
Depth Below NSL (m) | Material Type | Unit Weight (kN/m³) | Submerged Unit Weight (kN/m³) | Avg. SPT N (blows/ft) | Cohesion (kPa) | Angle of Internal Friction φ (deg)
0.0 – 0.75 | Fill Material | 16 | 6.2 | 10 | - | 29°
0.75 – 4.5 | Sabkha | - | - | 1 | - | -
4.5 – 12.0 | Silty Sand | 16.5 | 6.7 | 13 | - | 30°
12.0 – 15.0 | Lean Clay with Sand | 16.5 | 6.7 | 17 | 20 | -
TABLE 11: SOIL DESIGN PARAMETERS (Generalized)
Parameters | Granular Soils (Gravels & Sands) |  |  |  | Fine grained soils (Silts & Clays)
| Very loose to loose | Medium Dense | Dense | Very Dense | Very soft to Soft | Medium stiff | Hard
Cohesion (kN/m²) | - | - | - | - | 10-15 | 20-35 | 100-150
Angle of Internal Friction (Deg) | 28 | 32 | 35 | 38 | - | - | -
Bulk Unit Weight (kN/m³) | 14 | 18 | 19 | 20 | 16 | 17 | 21
Submerged Unit Weight (kN/m³) | 7 | 9 | 10 | 11 | 7 | 8 | 11
Static Modulus of Elasticity (kN/m²) | 8000 | 10,000 to 30,000 | 30,000 to 50,000 | 50,000 to 65,000 | 3000 | 6000 | 35,000 to 40,000
Modulus of subgrade reaction, Ks (kN/m³) | 6000 | 20000 | 25,000 to 35,000 | 35,000 to 45,000 | - | 10000 | 35,000 to 45,000
TABLE 12: BEARING CAPACITY AND SETTLEMENT VALUES (Option 1 - Improved Soil)
Type of Foundation | Length of Foundation (m) | Width of Foundation (m) | Recommended Allowable Bearing Capacity (kPa) | Modulus of subgrade reaction (kN/m³) | Settlement (mm)
Isolated | ≤4 | ≤4 | 150 | 18000 | ≤25
Raft | ≤30 | ≤30 | 130 | 11700 | ≤50
FOUNDATION OPTION 1: BEARING CAPACITY UNDER IMPROVED SOIL
Step 1 | Excavate the complete site to a depth of 5 meters from the existing level.
Step 2 | Backfill with seventeen (17) compacted layers of A-3 material having a thickness of 25cm each, compacted to a minimum of 75% relative density according to ASTM D-4253 & D-4254.
Step 3 | Place three (3) layers of crushed stone (gradation of Rockfill from 1 inch to 4 inches) having a thickness of 30cm each. Layers must be compacted to avoid settlement, until the stone column layer stabilizes and ensures it will not collapse.
Step 4 | Place a geotextile membrane of not less than 200 GSM on top of the rockfill layers.
Step 5 | Place a compacted layer of A-1-a material having a thickness of 60cm, compacted to 95% of the maximum dry density according to ASTM D1557.
Note | Zone load tests must be done by the approved testing agency to confirm the bearing capacity.
FOUNDATION OPTION 2: STONE COLUMN
Step 1 | Excavate the complete site to a depth of 0.5 meters from the existing level.
Step 2 | Construct Stone Columns to a depth of 12.0 meters from the excavation level.
Step 3 | Diameter of stone columns shall be 750mm to 900mm; spacing (edge-to-edge distance) should not be less than 2 to 3 times the column diameter.
Step 4 | Materials in stone columns: soundness >25%, LA Abrasion Value ≥ 40%, specific gravity >2.5, Absorption >2.
Step 5 | Place a layer of crushed stone (gradation of Rockfill from 1 inch to 4 inches) having a thickness of 25cm. Compact until stone column layer stabilizes.
Step 6 | Place a geotextile membrane of not less than 200 GSM on top of the rockfill layer.
Step 7 | Place 60 cm compacted layer of A-1-a material, compacted to 95% of maximum dry density according to ASTM D1557.
Note | Bearing capacity of stone columns shall not exceed 2.00 kg/cm² for Raft / Strip / Isolated footing connected with tie beam. Load tests must be done by approved testing agency.
OTHER DESIGN PARAMETERS
Active lateral earth pressure coefficient, Ka |  |  |  | 0.33
Passive lateral earth pressure coefficient, Kp |  |  |  | 3
At rest lateral earth pressure coefficient, Ko |  |  |  | 0.5
Permissible Excavation Slope |  |  |  | 1V : 2H
Minimum Scour Depth |  |  |  | 1.0 m below existing ground level
Modulus of Subgrade Reaction (Isolated/Strip) |  |  |  | Ks = 40 × FS × qa (kN/m³)
Modulus of Subgrade Reaction (Raft) |  |  |  | Ks = 30 × FS × qa (kN/m³)
Concrete Specifications Standard |  |  |  | 70-TMSS-03, Rev. 02
Backfill Specifications Standard |  |  |  | TCS-Q-113.02, Rev. 01 (General Fill - Class D)
Backfill Lift Thickness (max) |  |  |  | 300 mm
Backfill Compaction (free draining, 5-10% < #200) |  |  |  | 85% relative density (ASTM D-4253 & D-4254)
Backfill Compaction (5-10% passing 75-micron) |  |  |  | 95% maximum density (ASTM D-1557)
Compaction Equipment Recommended |  |  |  | 10-tonne compactor
Exposure Classification (per chemical analysis) |  |  |  | Very Severe

## 3. Logs of Boring
APPENDIX B: LOGS OF BORING - DETAILED SPT DATA
BH No. | Sample No. | Depth (m) | Strata | Strata Description | Blow Counts (6"-6"-6") | SPT N-Value (blows/300mm) | TCR (%) | RQD (%) | Fines % (< #200)
BH-1 | 1-1 | 0.75 | Fill | Brownish, Back Fill Material, Loose | 2-2-4 | 6 | N/A (Soil) | N/A (Soil) | 21.7
BH-1 | 1-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 3-3-4 | 7 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 0-4-5 | 9 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-7-8 | 15 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-6-11 | 17 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-10 | 10.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-9-10 | 19 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-11 | 12 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 6-6-9 | 15 | N/A (Soil) | N/A (Soil) | 86.9
BH-1 | 1-12 | 13.5 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Stiff to Very Stiff | 7-7-9 | 16 | N/A (Soil) | N/A (Soil) | -
BH-1 | 1-13 | 15 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Stiff to Very Stiff | 7-7-10 | 17 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-1 | 0.75 | Fill | Brownish, Back Fill Material, Medium Dense | 6-8-9 | 17 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 3-4-5 | 9 | N/A (Soil) | N/A (Soil) | 17.5
BH-2 | 2-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 4-7-7 | 14 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 2-4-7 | 11 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 6-8-10 | 18 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-10 | 10.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 6-7-9 | 16 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-11 | 12 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 7-7-9 | 16 | N/A (Soil) | N/A (Soil) | -
BH-2 | 2-12 | 13.5 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 6-8-8 | 16 | N/A (Soil) | N/A (Soil) | 96.2
BH-2 | 2-13 | 15 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 8-8-10 | 18 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-1 | 0.75 | Fill | Brownish, Back Fill Material, Loose | 2-3-3 | 6 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-2-3 | 5 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 5-5-9 | 14 | N/A (Soil) | N/A (Soil) | 8.6
BH-3 | 3-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 2-4-7 | 11 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 5-7-9 | 16 | N/A (Soil) | N/A (Soil) | -
BH-3 | 3-10 | 10 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 5-5-10 | 15 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-1 | 0.75 | Fill | Brownish, Back Fill Material, Loose | 1-4-4 | 8 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 2-3-4 | 7 | N/A (Soil) | N/A (Soil) | 18.9
BH-4 | 4-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 3-5-7 | 12 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-8-10 | 18 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 7-9-12 | 21 | N/A (Soil) | N/A (Soil) | -
BH-4 | 4-10 | 10 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 4-7-8 | 15 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-1 | 0.75 | Fill | Brownish, Back Fill Material, Loose | 2-3-3 | 6 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-0 | 1 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-3-3 | 6 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 3-3-7 | 10 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 3-3-8 | 11 | N/A (Soil) | N/A (Soil) | 35.8
BH-5 | 5-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 4-6-6 | 12 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-10 | 10.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 4-6-7 | 13 | N/A (Soil) | N/A (Soil) | -
BH-5 | 5-11 | 12 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-7-7 | 14 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-1 | 0.75 | Fill | Brownish, Back Fill Material, Medium Dense | 4-4-8 | 12 | N/A (Soil) | N/A (Soil) | 12.2
BH-1 (OUT) | 1-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-1 | 2 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 3-2-2 | 4 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 5-4-4 | 8 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-8 | 7.5 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 5-1-8 | 9 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 7-8-9 | 17 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-10 | 10.5 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 8-9-9 | 18 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-11 | 12 | Silty Sand | Dark Gray, Silty Sand, Very Loose to Medium Dense | 7-8-9 | 17 | N/A (Soil) | N/A (Soil) | -
BH-1 (OUT) | 1-12 | 13.5 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 6-10-10 | 20 | N/A (Soil) | N/A (Soil) | 82.1
BH-1 (OUT) | 1-13 | 15 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 7-9-9 | 18 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-1 | 0.75 | Fill | Brownish, Back Fill Material, Medium Dense | 4-10-7 | 17 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-2 | 1.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-3 | 2.25 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-0-1 | 1 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-4 | 3 | Sabkha | Dark Gray, Sabkha, Very Loose | 0-0-5 | 5 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-5 | 3.75 | Sabkha | Dark Gray, Sabkha, Very Loose | 1-1-1 | 2 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-6 | 4.5 | Sabkha | Dark Gray, Sabkha, Very Loose | 4-5-5 | 10 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-7 | 6 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 4-5-6 | 11 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-7b | 7.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 5-1-7 | 8 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-9 | 9 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 7-9-9 | 18 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-10 | 10.5 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 7-9-10 | 19 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-11 | 12 | Silty Sand | Dark Gray, Silty Sand, Loose to Medium Dense | 7-8-8 | 16 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-12 | 13.5 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 8-8-9 | 17 | N/A (Soil) | N/A (Soil) | -
BH-2 (OUT) | 2-13 | 15 | Lean Clay w/ Sand | Brownish, Lean Clay with Sand, Very Stiff | 5-8-10 | 18 | N/A (Soil) | N/A (Soil) | 96.2
NOTES:
• TCR (Total Core Recovery) and RQD (Rock Quality Designation) are reported as N/A because all boreholes encountered soil only (Fill, Sabkha, Silty Sand, Lean Clay) — no rock coring was performed.
• Atterberg Limits (LL, PL, PI) and Water Content data: see Sheet 4 "Lab Tests" for details on tested samples (full LL/PL/PI testing was not done on every SPT sample, only on representative samples).
• Fines % (passing #200 sieve) values shown are from sieve analysis on tested samples; "-" indicates no sieve analysis performed at that interval.
• SPT performed at 0.75m intervals to 3.0m depth, then 1.5m intervals thereafter (per ASTM D-1586-2011) using split spoon sampler.
• Drilling method: Mobile B 7 drilling rig using wash boring technique with bentonite slurry.

## 4. Lab Tests
APPENDIX C: LABORATORY TEST RESULTS
A. SIEVE ANALYSIS & ATTERBERG LIMITS - SUMMARY
Sample (BH-Depth) | Material | Date | % Gravel | % Coarse Sand | % Medium Sand | % Fine Sand | % Fines | PL | LL | PI | USCS | AASHTO
BH-1 @ 0.00m | Silty sand with gravel | 12-06-2024 | 32.6 | 9.6 | 13.5 | 22.6 | 21.7 | 0 | 0 | NP | SM | A-1-b
BH-1 @ 12.00m | Lean clay | 23-06-2024 | 1.8 | 2.9 | 2.5 | 5.9 | 86.9 | 16 | 32 | 16 | CL | A-6(13)
BH-2 @ 4.50m | Silty sand with gravel | 12-06-2024 | 25.9 | 3.8 | 7 | 45.8 | 17.5 | 0 | 0 | NP | SM | A-2-4(0)
BH-2 @ 13.50m | Lean clay | 23-06-2024 | 0 | 0.3 | 0.6 | 2.9 | 96.2 | 22 | 46 | 24 | CL | A-7-6(25)
BH-3 @ 6.00m | Poorly graded sand with silt | 12-06-2024 | 0.5 | 0.7 | 3.8 | 86.4 | 8.6 | 0 | 0 | NP | SP-SM | A-3
BH-4 @ 4.50m | Silty sand | 12-06-2024 | 0.9 | 3.1 | 5.8 | 71.3 | 18.9 | 0 | 0 | NP | SM | A-2-4(0)
BH-5 @ 7.50m | Silty sand | 12-06-2024 | 1.1 | 0.5 | 2.1 | 60.5 | 35.8 | 0 | 0 | NP | SM | A-4(0)
BH-1 (Out) @ 0.00m | Silty sand with gravel | 12-06-2024 | 15.5 | 5.4 | 18.9 | 48 | 12.2 | 0 | 0 | NP | SM | A-2-4(0)
BH-1 (Out) @ 13.50m | Lean clay with sand | 23-06-2024 | 6.4 | 1.6 | 1.8 | 8.1 | 82.1 | 19 | 39 | 20 | CL | A-6(16)
BH-2 (Out) @ 2.50m | Poorly graded sand with silt | 12-06-2024 | 0 | 0.5 | 3.4 | 87 | 9.1 | 0 | 0 | NP | SP-SM | A-3
BH-2 (Out) @ 15.00m | Lean clay | 23-06-2024 | 0 | 0.2 | 0.5 | 3.1 | 96.2 | 23 | 40 | 17 | CL | A-6(18)
B. SIEVE ANALYSIS - DETAILED % PASSING (Percent Finer)
Sample (BH-Depth) | 2" | 1-1/2" | 1" | 3/4" | 1/2" | 3/8" | #4 | #10 | #40 | #100 | #200
BH-1 @ 0.00m | 100 | 100 | 100 | 100 | 91.8 | 81.3 | 67.4 | 57.8 | 44.3 | 29 | 21.7
BH-1 @ 12.00m | 100 | 100 | 100 | 100 | 100 | 98.5 | 98.2 | 95.3 | 92.8 | 90.4 | 86.9
BH-2 @ 4.50m | 100 | 100 | 100 | 100 | 94.1 | 89.3 | 74.1 | 70.3 | 63.3 | 32.6 | 17.5
BH-2 @ 13.50m | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99.7 | 99.1 | 97.7 | 96.2
BH-3 @ 6.00m | 100 | 100 | 100 | 100 | 100 | 100 | 99.5 | 98.8 | 95 | 22.1 | 8.6
BH-4 @ 4.50m | 100 | 100 | 100 | 100 | 100 | 100 | 99.1 | 96 | 90.2 | 47.3 | 18.9
BH-5 @ 7.50m | 100 | 100 | 100 | 100 | 100 | 100 | 98.9 | 98.4 | 96.3 | 77.3 | 35.8
BH-1 (Out) @ 0.00m | 100 | 100 | 100 | 100 | 93.3 | 88.8 | 84.5 | 79.1 | 60.2 | 26.1 | 12.2
BH-1 (Out) @ 13.50m | 100 | 100 | 100 | 100 | 96.4 | 93.9 | 93.6 | 92 | 90.2 | 87.5 | 82.1
BH-2 (Out) @ 2.50m | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99.5 | 96.1 | 51.1 | 9.1
BH-2 (Out) @ 15.00m | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99.8 | 99.3 | 98 | 96.2
C. COMPACTION & CBR TEST RESULTS - SUMMARY (ASTM D-1557 / ASTM D-1883)
Sample | Depth (m) | Method | Max. Dry Density (kN/m³) | Optimum Moisture Content (%) | Blows = 10 - Dry Density (g/cc) | Blows = 25 - Dry Density (g/cc) | Blows = 56 - Dry Density (g/cc) | Soaked CBR @ 10 blows (%) | Soaked CBR @ 25 blows (%) | Soaked CBR @ 56 blows (%) | % of Max Dry Density | CBR @ 95% Max Dry Density (%)
CBR-01 | 0.3 | C | 17.8 | 14.3 | 1.223 | 1.505 | 1.828 | 22.2 | 28.4 | 35 | 1.723 | 33
CBR-02 | 0.3 | C | 18 | 15.4 | 1.527 | 1.667 | 1.847 | 23.2 | 28.7 | 35.5 | 1.741 | 31.5
Note: Max Dry Density values from Modified Proctor: CBR-01 = 1.814 g/cc (17.8 kN/m³), Optimum Moisture = 14.3%; CBR-02 = 1.833 g/cc (18.0 kN/m³), Optimum Moisture = 15.3% (CBR-02 page 2 reports 15.3%, page 1 reports 15.4%).
D. LABORATORY TESTS PERFORMED (Table 7)
Sr. # | Type of Test | No. of Tests | Test Method
1 | Sieve Analysis | 11 | ASTM D-422
2 | Atterberg Limits | 11 | ASTM D-4318
3 | Engineering Soil Classification | 11 | ASTM D-2487
4 | Chemical Analysis | 3 | BS 1377 Part 3
E. LABORATORY COMPACTION CHARACTERISTIC - MODIFIED EFFORT (ASTM D-1557) - CBR-01 SAMPLE
Project No. | GBL-GT-24136 | Sample Location | CBR-01 | Depth | 0.3 m | Method | C
Date | 12-Jun-24 | Date Tested | 12-Jun-24 | Date Completed | 13-Jun-24 | Ambient Temp. | 21 °C
Weight of Hammer | 10 lbs | Drop of Hammer | 18" | No. of Layers | 5 | No. of Blows | 56
Trial No. | Symbol | Unit | Trial 1 | Trial 2 | Trial 3 | Trial 4 | Trial 5
Wt. Mold. Wet Soil | B | g | 8770 | 9145 | 9508 | 9361 | 9152
Wt. Mold | C | g | 5181 | 5181 | 5181 | 5181 | 5181
Wt. Wet Soil (B-C) | D | g | 3589 | 3964 | 4327 | 4180 | 3971
Volume of Mold | E | cc | 2087 | 2087 | 2087 | 2087 | 2087
Wet Density (B-C)/E | F | g/cc | 1.72 | 1.899 | 2.073 | 2.003 | 1.903
Wt. Cont. + Wet Soil | H | g | 220 | 223 | 210.3 | 202.4 | 240
Wt. Cont. + Dry Soil | I | g | 212.9 | 210.9 | 193.4 | 181.4 | 208.3
Wt. Water (H-I) | L | g | 7.1 | 12.1 | 16.9 | 21 | 31.7
Wt. Container | M | g | 83.4 | 84.1 | 75.3 | 72.7 | 62.7
Wt. Dry Soil (I-M) | N | g | 129.5 | 126.8 | 118.1 | 108.7 | 145.6
Moisture Content (100×L/N) | P | % | 5.5 | 9.5 | 14.3 | 19.3 | 21.8
Dry Density 100×F/(100+P) | R | g/cc | 1.63 | 1.734 | 1.814 | 1.679 | 1.563
Dry Density | O | kN/m³ | 16 | 17 | 17.8 | 16.5 | 15.3
Parameter | Value | Unit
Maximum Dry Density | 17.8 | kN/m³
Maximum Dry Density | 1.814 | g/cc
Optimum Moisture Content | 14.3 | %
F. LABORATORY COMPACTION CHARACTERISTIC - MODIFIED EFFORT (ASTM D-1557) - CBR-02 SAMPLE
Project No. | GBL-GT-24136 | Sample Location | CBR-02 | Depth | 0.3 m | Method | C
Date | 12-Jun-24 | Date Tested | 12-Jun-24 | Date Completed | 13-Jun-24 | Ambient Temp. | 21 °C
Weight of Hammer | 10 lbs | Drop of Hammer | 18" | No. of Layers | 5 | No. of Blows | 56
Trial No. | Symbol | Unit | Trial 1 | Trial 2 | Trial 3 | Trial 4 | Trial 5
Wt. Mold. Wet Soil | B | g | 8366 | 8842 | 9208 | 9396 | 9192
Wt. Mold | C | g | 4986 | 4986 | 4986 | 4986 | 4986
Wt. Wet Soil (B-C) | D | g | 3380 | 3856 | 4222 | 4410 | 4206
Volume of Mold | E | cc | 2085 | 2085 | 2085 | 2085 | 2085
Wet Density (B-C)/E | F | g/cc | 1.621 | 1.849 | 2.025 | 2.115 | 2.017
Wt. Cont. + Wet Soil | H | g | 236.6 | 248.1 | 281.1 | 255.7 | 299.5
Wt. Cont. + Dry Soil | I | g | 230.6 | 234 | 257.4 | 229.6 | 258
Wt. Water (H-I) | L | g | 6 | 14.1 | 23.7 | 26.1 | 41.5
Wt. Container | M | g | 56.7 | 63 | 57.2 | 59.8 | 60.9
Wt. Dry Soil (I-M) | N | g | 173.9 | 171 | 200.2 | 169.8 | 197.1
Moisture Content (100×L/N) | P | % | 3.5 | 8.2 | 11.8 | 15.4 | 21.1
Dry Density 100×F/(100+P) | R | g/cc | 1.567 | 1.709 | 1.811 | 1.833 | 1.666
Dry Density | O | kN/m³ | 15.4 | 16.8 | 17.8 | 18 | 16.3
Parameter | Value | Unit
Maximum Dry Density | 18 | kN/m³
Maximum Dry Density | 1.833 | g/cc
Optimum Moisture Content | 15.4 | %
Optimum Moisture Content (CBR-02 page 2) | 15.3 | %
G. CALIFORNIA BEARING RATIO (ASTM D-1883) - CBR-01 SAMPLE - FULL DETAIL
Project No. | GBL-GT-24136 | Sample No. | CBR-01 | Date | 20-Jun-24 | Date Tested | 20-Jun-24
Date Completed | 24-Jun-24 | Water Temperature | 20 | Correction Factor | 4.201 | Plunger Area (cm) | 19.35
Molding Moisture Content
Parameter | Unit | Test 1 (10 blows) | Test 2 (25 blows) | Test 3 (56 blows)
Mold Volume | cm³ | 3264 | 3248 | 3271
Mass Wet Soil + Can | g | 258 | 245 | 238.2
Mass Sample + Mold | g | 10695 | 11957 | 13105
Mass Dry Soil + Can | g | 231 | 219.8 | 213.1
Mass Mold | g | 6137 | 6375 | 6269
Mass Moisture (A-B) | g | 27 | 25.2 | 25.1
Mass Sample | g | 4558 | 5582 | 6836
Mass Can | g | 41.2 | 42.5 | 37.6
Unit Wet Mass | g/cm³ | 1.396 | 1.719 | 2.09
Mass Dry Soil (B-D) | g | 189.8 | 177.3 | 175.5
Percent Moisture | % | 14.2 | 14.2 | 14.3
Percent Moisture (C/E×100) | % | 14.2 | 14.2 | 14.3
Unit Dry Mass | g/cm³ | 1.223 | 1.505 | 1.828
Penetration vs Load (Stress) Data
Penetration (mm) | Std Load (Kg/cm²) | Test 1 Total Load (Kg) | Test 1 Unit Load (Kg/cm²) | Test 1 Corr. Load (Kg/cm²) | Test 1 % CBR | Test 2 Total Load (Kg) | Test 2 Unit Load (Kg/cm²) | Test 2 Corr. Load (Kg/cm²) | Test 2 % CBR | Test 3 Total Load (Kg) | Test 3 Unit Load (Kg/cm²) | Test 3 % CBR
0 |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
0.64 |  | 126 | 6.5 |  |  | 168 | 8.7 |  |  | 235.3 | 12.2
1.27 |  | 201.7 | 10.4 |  |  | 247.9 | 12.8 |  |  | 331.9 | 17.2
1.9 |  | 252.1 | 13 |  |  | 315.1 | 16.3 |  |  | 407.5 | 21.1
2.54 |  | 302.5 | 15.6 | 15.6 | 22.2 | 386.5 | 20 | 20 | 28.4 | 478.9 | 24.8 | 35.2
3.81 |  | 352.9 | 18.2 |  |  | 428.5 | 22.1 |  |  | 525.2 | 27.1
5.08 |  | 390.7 | 20.2 | 20.2 | 19.1 | 453.7 | 23.4 | 23.4 | 22.2 | 542 | 28 | 26.5
7.62 |  | 403.3 | 20.8 |  |  | 457.9 | 23.7 |  |  | 550.4 | 28.4
Swell Data
Parameter | Unit | Test 1 (10 blows) | Test 2 (25 blows) | Test 3 (56 blows)
Mold No. |  | 1 | 2 | 3
Final Height | mm | 13 | 9 | 4.9
Initial Height | mm | 0 | 0 | 0
Difference | mm | 13 | 9 | 4.9
Sample Length | mm | 116.8 | 116.1 | 115.95
Percent Swell | % | 11.13 | 7.75 | 4.23
Parameter | Blows = 10 | Blows = 25 | Blows = 56
Dry Density (g/cc) | 1.223 | 1.505 | 1.828
Soaked CBR (%) | 22.2 | 28.4 | 35
Maximum Dry Density | 1.814 | g/cc
Optimum Moisture Content | 14.3 | %
% of Maximum Dry Density (target) | 1.723
CBR @ 95% of Maximum Dry Density | 33 | %
H. CALIFORNIA BEARING RATIO (ASTM D-1883) - CBR-02 SAMPLE - FULL DETAIL
Project No. | GBL-GT-24136 | Sample No. | CBR-02 | Date | 20-Jun-24 | Date Tested | 20-Jun-24
Date Completed | 24-Jun-24 | Water Temperature | 20 | Correction Factor | 4.201 | Plunger Area (cm) | 19.35
Molding Moisture Content
Parameter | Unit | Test 1 (10 blows) | Test 2 (25 blows) | Test 3 (56 blows)
Mold Volume | cm³ | 3215 | 3249 | 3227
Mass Wet Soil + Can | g | 205.3 | 202.6 | 216.5
Mass Sample + Mold | g | 11651 | 12405 | 13121
Mass Dry Soil + Can | g | 184 | 183 | 194.6
Mass Mold | g | 5982 | 6158 | 6251
Mass Moisture (A-B) | g | 21.3 | 19.6 | 21.9
Mass Sample | g | 5669 | 6247 | 6870
Mass Can | g | 46.3 | 55.4 | 51.3
Unit Wet Mass | g/cm³ | 1.763 | 1.923 | 2.129
Mass Dry Soil (B-D) | g | 137.7 | 127.6 | 143.3
Percent Moisture | % | 15.5 | 15.4 | 15.3
Percent Moisture (C/E×100) | % | 15.5 | 15.4 | 15.3
Unit Dry Mass | g/cm³ | 1.527 | 1.667 | 1.847
Penetration vs Load (Stress) Data
Penetration (mm) | Std Load (Kg/cm²) | Test 1 Total Load (Kg) | Test 1 Unit Load (Kg/cm²) | Test 1 Corr. Load (Kg/cm²) | Test 1 % CBR | Test 2 Total Load (Kg) | Test 2 Unit Load (Kg/cm²) | Test 2 Corr. Load (Kg/cm²) | Test 2 % CBR | Test 3 Total Load (Kg) | Test 3 Unit Load (Kg/cm²) | Test 3 % CBR
0 |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
0.64 |  | 109.2 | 5.6 |  |  | 180.7 | 9.3 |  |  | 218.5 | 11.3
1.27 |  | 189.1 | 9.8 |  |  | 264.7 | 13.7 |  |  | 315.1 | 16.3
1.9 |  | 256.3 | 13.2 |  |  | 331.9 | 17.2 |  |  | 399.1 | 20.6
2.54 |  | 315.1 | 16.3 | 16.3 | 23.2 | 390.7 | 20.2 | 20.2 | 28.7 | 483.1 | 25 | 35.5
3.81 |  | 357.1 | 18.5 |  |  | 453.7 | 23.4 |  |  | 550.4 | 28.4
5.08 |  | 382.3 | 19.8 | 19.8 | 18.7 | 504.1 | 26.1 | 26.1 | 24.7 | 609.2 | 31.5 | 29.8
7.62 |  | 399.1 | 20.6 |  |  | 525.2 | 27.1 |  |  | 626 | 32.4
Swell Data
Parameter | Unit | Test 1 (10 blows) | Test 2 (25 blows) | Test 3 (56 blows)
Mold No. |  | 1 | 2 | 3
Final Height | mm | 16 | 11 | 6
Initial Height | mm | 0 | 0 | 0
Difference | mm | 16 | 11 | 6
Sample Length | mm | 116.41 | 116.15 | 116.33
Percent Swell | % | 13.74 | 9.47 | 5.16
Parameter | Blows = 10 | Blows = 25 | Blows = 56
Dry Density (g/cc) | 1.527 | 1.667 | 1.847
Soaked CBR (%) | 23.2 | 28.7 | 35.5
Maximum Dry Density | 1.833 | g/cc
Optimum Moisture Content | 15.3 | %
% of Maximum Dry Density (target) | 1.741
CBR @ 95% of Maximum Dry Density | 31.5 | %
NOTES (Compaction & CBR):
• Modified Effort Compaction per ASTM D-1557, Method C: Hammer 10 lbs, Drop 18", 5 layers, 56 blows per layer.
• California Bearing Ratio per ASTM D-1883: Three molds compacted at 10, 25, and 56 blows per layer.
• Standard Loads at 2.54 mm and 5.08 mm penetration: 70.31 kg/cm² and 105.46 kg/cm² respectively (corresponds to 1000 psi and 1500 psi).
• Correction factor = 4.201; Plunger area = 19.35 cm² (3-inch diameter).
• Soaked CBR values reported after sample soaking; swell measured during soaking period.
• CBR @ 95% Max Dry Density derived by interpolation from the dry density vs CBR curve.

## 5. ERT Results
APPENDIX D: ELECTRICAL RESISTIVITY TEST (ERT) RESULTS
ERT LOCATIONS SUMMARY (Apparent Resistivity Min/Max)
ERT # | Northing | Easting | Min Apparent Resistivity (Ωm) | Max Apparent Resistivity (Ωm) | Corrosivity Range
ERT-1 | 2443933.1866 | 502979.8701 | 0 | 0.15 | Very Severe
ERT-2 | 2443922.2288 | 502953.4984 | 0 | 0.15 | Very Severe
ERT-3 | 2443944.6093 | 502963.0234 | 0 | 0.23 | Very Severe
ERT-4 | 2443939.4128 | 503001.2742 | 0 | 0.11 | Very Severe
ERT-5 | 2443913.6857 | 502995.6074 | 0 | 0.18 | Very Severe
ERT-6 | 2443899.0896 | 502970.2246 | 0 | 0.13 | Very Severe
TABLE 5: CORRELATION BETWEEN CORROSIVITY & SOIL RESISTIVITY (per JD Palmer, 1974)
Soil Resistivity (Ωm) | Corrosivity
0 - 10 | VERY SEVERE
11 - 20 | SEVERE
21 - 50 | MODERATE
51 - 100 | MILD
101+ | VERY MILD
DETAILED FIELD MEASUREMENTS - APPARENT RESISTIVITY (Ωm) at each Electrode Spacing & Direction
ERT # | Coordinates | Electrode Spacing (m) | N-S (Ωm) | E-W (Ωm) | NE-SW (Ωm) | NW-SE (Ωm) | Average (Ωm) | Classification
ERT-1 | 2443933.1866 N, 502979.8701 E | 0.5 | 0.129 | 0.113 | 0.097 | 0.132 | 0.118 | Very Severe
|  | 1 | 0.132 | 0.126 | 0.113 | 0.094 | 0.116 | Very Severe
|  | 2 | 0.113 | 0.126 | 0.151 | 0.101 | 0.123 | Very Severe
|  | 3 | 0.038 | 0.094 | 0.057 | 0.075 | 0.066 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
ERT-2 | 2443922.2288 N, 502953.4984 E | 0.5 | 0.088 | 0.097 | 0.094 | 0.079 | 0.09 | Very Severe
|  | 1 | 0.113 | 0.126 | 0.094 | 0.088 | 0.105 | Very Severe
|  | 2 | 0.088 | 0.151 | 0.101 | 0.101 | 0.11 | Very Severe
|  | 3 | 0.057 | 0.075 | 0.057 | 0.038 | 0.057 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
ERT-3 | 2443944.6093 N, 502963.0234 E | 0.5 | 0.157 | 0.135 | 0.145 | 0.126 | 0.141 | Very Severe
|  | 1 | 0.232 | 0.195 | 0.17 | 0.214 | 0.203 | Very Severe
|  | 2 | 0.113 | 0.138 | 0.101 | 0.101 | 0.113 | Very Severe
|  | 3 | 0.038 | 0.075 | 0.094 | 0.057 | 0.066 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
ERT-4 | 2443939.4128 N, 503001.2742 E | 0.5 | 0.063 | 0.085 | 0.075 | 0.072 | 0.074 | Very Severe
|  | 1 | 0.075 | 0.113 | 0.094 | 0.107 | 0.097 | Very Severe
|  | 2 | 0.113 | 0.088 | 0.113 | 0.101 | 0.104 | Very Severe
|  | 3 | 0.075 | 0.057 | 0.057 | 0.094 | 0.071 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
ERT-5 | 2443913.6857 N, 502995.6074 E | 0.5 | 0.116 | 0.094 | 0.11 | 0.088 | 0.102 | Very Severe
|  | 1 | 0.132 | 0.113 | 0.145 | 0.107 | 0.124 | Very Severe
|  | 2 | 0.176 | 0.126 | 0.151 | 0.138 | 0.148 | Very Severe
|  | 3 | 0.17 | 0.132 | 0.132 | 0.151 | 0.146 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
ERT-6 | 2443899.0896 N, 502970.2246 E | 0.5 | 0.082 | 0.063 | 0.085 | 0.066 | 0.074 | Very Severe
|  | 1 | 0.094 | 0.107 | 0.088 | 0.075 | 0.091 | Very Severe
|  | 2 | 0.126 | 0.113 | 0.101 | 0.113 | 0.113 | Very Severe
|  | 3 | 0.094 | 0.057 | 0.094 | 0.075 | 0.08 | Very Severe
|  | 4 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 5 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 6 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 7 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 8 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 9 | 0 | 0 | 0 | 0 | 0 | Very Severe
|  | 10 | 0 | 0 | 0 | 0 | 0 | Very Severe
NOTES:
• Method: Wenner Four-Electrode Method per ASTM G57 / IEEE-81
• Instrument: DET4TD2 Megger Earth Tester (S/N 1000347102246564), 4 stainless-steel electrodes, 4 insulated wire conductors
• Test conducted at 6 locations in 8 directions (4 directions reported: N-S, E-W, NE-SW, NW-SE) at electrode spacings 0.5, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10 m
• Date Tested: 06-Jun-2024
• Apparent Resistivity formula (Wenner): ρa = (4πaR) / [1 + 2a/√(a²+4b²) − a/√(a²+b²)]; for a > 10b: ρa ≈ 2πaR
DETAILED FIELD MEASUREMENTS - MEASURED RESISTANCE (Ω) at each Electrode Spacing & Direction
ERT # | Coordinates | Electrode Spacing (m) | N-S (Ω) | E-W (Ω) | NE-SW (Ω) | NW-SE (Ω)
ERT-1 | 2443933.1866 N, 502979.8701 E | 0.5 | 0.041 | 0.036 | 0.031 | 0.042
|  | 1 | 0.021 | 0.02 | 0.018 | 0.015
|  | 2 | 0.009 | 0.01 | 0.012 | 0.008
|  | 3 | 0.002 | 0.005 | 0.003 | 0.004
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
ERT-2 | 2443922.2288 N, 502953.4984 E | 0.5 | 0.028 | 0.031 | 0.03 | 0.025
|  | 1 | 0.018 | 0.02 | 0.015 | 0.014
|  | 2 | 0.007 | 0.012 | 0.008 | 0.008
|  | 3 | 0.003 | 0.004 | 0.003 | 0.002
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
ERT-3 | 2443944.6093 N, 502963.0234 E | 0.5 | 0.05 | 0.043 | 0.046 | 0.04
|  | 1 | 0.037 | 0.031 | 0.027 | 0.034
|  | 2 | 0.009 | 0.011 | 0.008 | 0.008
|  | 3 | 0.002 | 0.004 | 0.005 | 0.003
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
ERT-4 | 2443939.4128 N, 503001.2742 E | 0.5 | 0.02 | 0.027 | 0.024 | 0.023
|  | 1 | 0.012 | 0.018 | 0.015 | 0.017
|  | 2 | 0.009 | 0.007 | 0.009 | 0.008
|  | 3 | 0.004 | 0.003 | 0.003 | 0.005
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
ERT-5 | 2443913.6857 N, 502995.6074 E | 0.5 | 0.037 | 0.03 | 0.035 | 0.028
|  | 1 | 0.021 | 0.018 | 0.023 | 0.017
|  | 2 | 0.014 | 0.01 | 0.012 | 0.011
|  | 3 | 0.009 | 0.007 | 0.007 | 0.008
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
ERT-6 | 2443899.0896 N, 502970.2246 E | 0.5 | 0.026 | 0.02 | 0.027 | 0.021
|  | 1 | 0.015 | 0.017 | 0.014 | 0.012
|  | 2 | 0.01 | 0.009 | 0.008 | 0.009
|  | 3 | 0.005 | 0.003 | 0.005 | 0.004
|  | 4 | 0 | 0 | 0 | 0
|  | 5 | 0 | 0 | 0 | 0
|  | 6 | 0 | 0 | 0 | 0
|  | 7 | 0 | 0 | 0 | 0
|  | 8 | 0 | 0 | 0 | 0
|  | 9 | 0 | 0 | 0 | 0
|  | 10 | 0 | 0 | 0 | 0
NOTE: Apparent Resistivity is calculated from Measured Resistance using the Wenner formula: ρa = (4πaR) / [1 + 2a/√(a²+4b²) − a/√(a²+b²)]; for a > 10b: ρa ≈ 2πaR. The measured resistance values above are the raw field readings (in ohms) from the DET4TD2 Megger Earth Tester.

## 6. TRT Results
APPENDIX E: THERMAL RESISTIVITY TEST (TRT) RESULTS
TRT LOCATIONS SUMMARY (Table 6)
TRT # | Northing | Easting | Sample Depth (m) | Water Content (%) | Dry Density (g/cc) | Sample Temp (°C) | Thermal Conductivity (W/mK) | Thermal Resistivity (mK/W)
TR-1 | 2443918.9003 | 502955.1028 | 3 | 2 | 1.698 | 24.7 | 0.301 | 3.322
TR-2 | 2443943.5913 | 502958.5427 | 2 | 2 | 1.702 | 25.1 | 0.304 | 3.289
TR-3 | 2443909.8393 | 502998.0263 | 1 | 2 | 1.706 | 24.6 | 0.345 | 2.899
TR-4 | 2443901.8217 | 502984.0351 | 1 | 2 | 1.698 | 25.3 | 0.392 | 2.551
DETAILED TIME vs TEMPERATURE DATA (Heating Curves)
Time (Sec.) | TR-1 Temp (°C) | TR-2 Temp (°C) | TR-3 Temp (°C) | TR-4 Temp (°C)
10 | 28.4 | 28.6 | 28 | 28.8
20 | 29.4 | 29.7 | 29 | 29.7
30 | 30.2 | 30.4 | 29.7 | 30.4
40 | 30.7 | 30.9 | 30.1 | 30.8
50 | 31 | 31.2 | 30.4 | 31
60 | 31.3 | 31.4 | 30.6 | 31.2
70 | 31.5 | 31.7 | 30.8 | 31.4
80 | 31.6 | 31.8 | 30.9 | 31.5
90 | 31.8 | 31.9 | 31.1 | 31.6
NOTES:
• Method: Thermal Needle Probe per ASTM D5334 / IEEE Std 442™-2017
• Instrument: TLS 100mm Thermal Resistivity Machine by Thermtest Instruments
• Date Tested: 06-Jun-2024; Date Completed: 23-Jun-2024
• Ambient Temperature: 21 °C
• Formula: ρ = 4π(T₂-T₁) / (q × ln(t₂/t₁)) where ρ = thermal resistivity (K·m/W), q = heat dissipated per unit length (W/m), t = elapsed time (min)
• Delta T values: TR-1 = 6.9 °C, TR-2 = 6.9 °C, TR-3 = 6.3 °C, TR-4 = 6.3 °C
• Resistance Ω (mK/W): TR-1 = 3.32226, TR-2 = 3.28947, TR-3 = 2.89855, TR-4 = 2.55102

## 7. Chemical Analysis
CHEMICAL ANALYSIS RESULTS (BS 1377 Part 3)
TABLE 8: CHEMICAL TEST RESULTS - SUMMARY RANGE
Parameter | Value Range / Result
pH | 7.90 – 8.20
Sulphates SO₄ (PPM) | 5810 – 8515
Chlorides (%) | 0.510 – 0.705
Magnesium (PPM) | 571 – 954
Site Exposure Classification | VERY SEVERE
DETAILED CHEMICAL ANALYSIS RESULTS BY SAMPLE
BH No. | Depth (m) | pH | Sulphate Content SO₄ (PPM) | Chloride Content (%) | Magnesium Content (PPM)
BH-1 | 0.75 | 7.9 | 5810 | 0.705 | 954
BH-3 | 4.5 | 8.1 | 6970 | 0.635 | 795
BH-2 (Out) | 6 | 8.2 | 8515 | 0.51 | 571
TABLE 8B: CONCRETE REQUIREMENTS UNDER VERY SEVERE EXPOSURE (per 70-TMSS-03 Rev.02)
Exposure Type | Cement Type | Pozzolanic Admixture | Max W/BM Ratio | Min Binding Material (kg/m³) | Max Cl in Concrete (%)
Very Severe (Mg>1000) | Type I C₃A 8-14% | Fly Ash | 0.36 | 390 | 0.1
Very Severe (Mg>1000) | Type I C₃A 8-14% | Silica Fumes | 0.4 | 390 | 0.1
Severe (Mg>1000) | Type I C₃A 8-14% | Fly Ash | 0.36 | 390 | 0.1
Severe (Mg<1000) | Type I C₃A 8-14% | Silica Fumes | 0.4 | 390 | 0.1
Severe | Type V | Fly Ash | 0.36 | 390 | 0.1
Moderate | Type II / Type I C₃A 5-8% | - | 0.4 | 350 | 0.1
Moderate | Type V | - | 0.4 | 350 | 0.1
NOTES:
• Min Concrete Strength (f'c): 38 MPa / 5500 psi for Very Severe and Severe Exposure
• Min Concrete Strength (f'c): 28 MPa / 4000 psi for Moderate Exposure
• BM = Binding Material = Cement + Pozzolanic Materials (Fly Ash or Silica Fumes)
• Foundations and external surfaces shall be protected with waterproofing membrane/coating
• Date of Chemical Test: 20-Jun-24 to 23-Jun-24
• Ambient Temperature during test: 22 °C
• Material with sulfate/chloride content greater than existing soil shall NOT be used as backfill